## New b-form
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
B- FORMS OF IF POINTS
NAME OF THE STATION: 66/11 KV MUSS Kembodi | [7 empty] | IF POINT SL.NO
NAME OF THE DIVISION: TL & SS Division Kolar | [7 empty] | MONTH :March-2025
Sl. No. | SUB-STATION NAME | PT Capacity/Name of the EHT/ Name of the IPP with Voltage Class | INTERFACE POINT | METER TYPE | CT RATIO | METER SL.NO | FLOW TYPE | MF | INITIAL | FINAL | CONSUMPTION (IN KWH) | Remarks
1 | 66/11 KV sub station Kembodi | 11KV/110V | 11kV Bank-1 | Secure, DLMS,P3E | 800/1 A | Q0255800 | FROM KPTCL | 80000 | 110.673 | 145.973 | 2824000
[7 empty] | TO KPTCL |  | 0 | 0 | 0
2 |  | 11KV/110V | 11kV Bank-2 | Secure, DLMS,P3E | 800/1 A | Q0247345 | FROM KPTCL | 80000 | 1079.65 | 1109.129 | 2358320
3 |  |  | AUX-1 | Secure, non DLMS, | 150/5 A | BES 18311 | FROM KPTCL | 1 | 229280.7 | 230342.6 | 1061.9
4 |  |  | AUX-2 | Nill | Nil | Nil | FROM KPTCL | Nil | Nil | Nil | 0
[7 empty] | FROM KPTCL |  |  |  | 0
5 |  | Nil | EHT | Nil | Nil | Nil | FROM KPTCL | Nil | Nil | Nil | Nil
6 |  | Nil | IPP | Nil | Nil | Nil | TO KPTCL | Nil | Nil | Nil | Nil
Transformer wise energy audit ANNEXURE
Sl. No. | SUB-STATION NAME | TRANSFORMER | Connected Bank | METER TYPE | CT RATIO | METER SL.NO | FLOW TYPE | MF | INITIAL | FINAL | CONSUMPTION
1 | 66/11kv s/s Kembodi | 12.5 MVA TRANSFORMER-1 (TAL make) | Bank-1 | Secure NON-DLMS | 200-1 | KAU06672 | FROM KPTCL | 2000 | 169134.3 | 170572.9 | 2877200
2 |  | 8MVA TRANSFORMER-2 (SPEC Make) | Bank-2 | Secure NON-DLMS | 100-1 | KAU06673 | FROM KPTCL | 1000 | 240269.1 | 242641 | 2371900
| Assistant Engineer (Ele.) |  |  |  |  | Assistant Executive Engineer(Ele.) |  |  |  |  | Executive Engineer (Ele.)
| 66/11KV S/S Kembodi. |  |  |  |  | 220/66/11kV R/S, KPTCL, |  |  |  |  | TL&SS Division, KPTCL,
ASSESSED CONSUMPTION (1% TRANSFORMER LOSSES)IN M.U
TRANSFORMER HV READING-1% TRANSFORMER LOSS =IF POINT CONSUMPTION IN M.U

## consumption
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Details of Energy Consumption, Station Peak Load, Interruption, Major Equipments Commissioned / Failed of 66/11 KV MUSS Kembodi For The Month of March-2025
Slno | Nameof I/C Line and O/G 66KV Transformer, 11KV Bank,Feeders | Connected CT's Ratio | Mtr Slno. | Reading |  | Diffrence | Meter Constant | Consumption | Peak Load |  |  |  | Maximum Voltage |  |  |  | Minimum Voltage | [11 empty] | Power Supply given
|  |  |  | Present | Previous |  |  |  | Amps | MWs | Date | Time | KV | Date | Time | TAP | KV | Date | Time | TAP | LC |  | Faulty |  | Load Shed |  | MSF |  | Open ∆ |  | 3 Phase
[22 empty] | Dur | No | Dur | No | Dur | No | Dur | No | Dur | No | Dur | bar: Minimum Voltage LC
|  | 1 |  | 2 | 3 | 4 | 5 | 6 | [18 empty] | 2 | 7:52
| 66KV I/C Line Kolar | 400/1 | KAU06663 | 1073526 | 1070902 | 2624 | 2000 | 5248000 | 144 | 14.4 | 3 | 13 | 66.9 | 1 | 16 |  | 63.5 | 21 | 6
| 66 KV OG Line Nangli | 400/1 | KAU06666 | 844622 | 844622 | 0 | 2000 | 0
Total I/Cline consumption
| Power Transformer I | 200/1 | KAU06672 | 170572.9 | 169134.3 | 1438.6 | 2000 | 2877200 | Peak Load Amps: 90; Peak Load MWs: 9; Peak Load Date: 22; Peak Load Time: 13; Maximum Voltage TAP: 10; Minimum Voltage TAP: 5; Minimum Voltage LC: 1 | 1:15
| Power Transformer II | 100/1 | KAU06673 | 242641 | 240269.1 | 2371.9 | 1000 | 2371900 | Peak Load Amps: 64; Peak Load MWs: 6.4; Peak Load Date: 20; Peak Load Time: 14; Maximum Voltage TAP: 8; Minimum Voltage TAP: 5
5249100
| 11 KV Bank I DLMS | 800/1 | Q0255800 | 145.973 | 110.673 | 35.3 | 80000 | 2824000 | 540 | 9 | 22 | 13 | 11.8 | 1 | 16 |  | 10.7 | 6 | 5 |  | 1 | 1:15
|  | Import |  | 0 | 0 | 0 | 80000 | 0
| Bank-1 consumption | [6 empty] | 2824000 | [25 empty] | FEEDERS | TOTAL HURS
| F 1 - Huttur DLMS | 200/1 | Q0247239 | 2046.477 | 2025.353 | 21.124 | 20000 | 422480 | Peak Load Amps: 80; Peak Load MWs: 1.3; Peak Load Date: 20; Peak Load Time: 13; Minimum Voltage LC: 23 | 12:45 | 21 | 8:20 | [6 empty] | 67 | 722:55 |  | F1 | 744:00 |  | 744:00
| F 2 - Abbani DLMS | 200/1 | Q0247366 | 1136.413 | 1107.706 | 28.707 | 20000 | 574140 | Peak Load Amps: 200; Peak Load MWs: 3.3; Peak Load Date: 1; Peak Load Time: 14; Minimum Voltage LC: 1 | 0:10 | 12 | 10:40 | 78 | 517:40 |  |  |  |  | 82 | 215:30 |  | F2 | 740:00 |  | 744:00
| F 3 - Kembodi DLMS | 200/1 | Q0247359 | 890.404 | 857.185 | 33.219 | 20000 | 664380 | Peak Load Amps: 200; Peak Load MWs: 3.3; Peak Load Date: 1; Peak Load Time: 9; Minimum Voltage LC: 6 | 3:45 | 16 | 15:25 | 76 | 510:50 |  |  |  |  | 90 | 214:00 |  | F3 | 744:00 |  | 744:00
| F 4 - Holali DLMS | 200/1 | Q0255828 | 137.114 | 107.231 | 29.883 | 20000 | 597660 | Peak Load Amps: 80; Peak Load MWs: 1.3; Peak Load Date: 21; Peak Load Time: 10; Minimum Voltage LC: 30 | 12:20 | 37 | 26:50 | [6 empty] | 87 | 704:50 |  | F4 | 744:00 |  | 744:00
|  | Import |  | 0 | 0 | 0 | 20000 | 0
| F-9 Shapur DLMS | 200/1 | Q0247188 | 994.012 | 966.459 | 27.553 | 20000 | 551060 | Peak Load Amps: 200; Peak Load MWs: 3.3; Peak Load Date: 11; Peak Load Time: 9; Minimum Voltage LC: 1 | 0:15 | 11 | 13:50 | 77 | 512:55 |  |  |  |  | 85 | 217:00 |  | F9 | 744:00 |  | 744:00
| Bank-1 feeders consumption | [6 empty] | 2809720
| 11 KV Bank II DLMS | 800/1 | Q0247345 | 1109.129 | 1079.65 | 29.479 | 80000 | 2358320 | 384 | 6.4 | 20 | 14 | 11.8 | 1 | 16 | 10.7
| F5 - Lotus DLMS | 200/1 | Q0247368 | 1225.759 | 1183.663 | 42.096 | 20000 | 841920 | Peak Load Amps: 170; Peak Load MWs: 2.8; Peak Load Date: 4; Peak Load Time: 11; Minimum Voltage LC: 26 | 10:35 | 27 | 9:40 | [6 empty] | 73 | 723:45 |  | F5 | 744:00 |  | 744:00
| F6 - Vittapanahalli DLMS | 200/1 | Q0246984 | 1132.932 | 1100.929 | 32.003 | 20000 | 640060 | Peak Load Amps: 200; Peak Load MWs: 3.3; Peak Load Date: 2; Peak Load Time: 12; Minimum Voltage LC: 1 | 0:20 | 5 | 7:15 | 76 | 519:25 |  |  |  |  | 82 | 217:00 |  | F6 | 744:00 |  | 744:00
| F7 - Seesandra DLMS | 200/1 | Q0247212 | 1011.801 | 996.64 | 15.161 | 20000 | 303220 | Peak Load Amps: 70; Peak Load MWs: 1.1; Peak Load Date: 8; Peak Load Time: 11; Minimum Voltage LC: 37 | 14:35 | 14 | 1:45 | [6 empty] | 72 | 727:40 |  | F7 | 744:00 |  | 744:00
| F8 - Ramasandra DLMS | 200/1 | Q0245131 | 40.377 | 11.656 | 28.721 | 20000 | 574420 | Peak Load Amps: 200; Peak Load MWs: 3.3; Peak Load Date: 1; Peak Load Time: 13; Minimum Voltage LC: 1 | 0:15 | 4 | 1:30 | 78 | 525:15 |  |  |  |  | 81 | 217:00 |  | F8 | 744:00 |  | 744:00
| Bank-2 feeders consumption | [6 empty] | 2359620
| Bank-1 & Bank-2 consumption | [6 empty] | 5182320
| CAPACITOR BANK I | 200/1
| CAPACITOR BANK II | 200/1 | [34 empty] | 5.1823
| STN Auxualarry/Peak load |  | BES18311 | 230342.6 | 229280.7 | 1061.9 | 1 | 1061.9 | Peak Load Amps: 864; Peak Load MWs: 14.4; Peak Load Date: 3; Peak Load Time: 13
| Daily maintenance:- Daily | [5 empty] | Weekly maintenance on :- |  | Peak Load Time: 3/03,10/03,17/03,24/03,&31/03/2025; Minimum Voltage Time: Quarterly Maintenance |  |  |  | Nill
Note:-1) 66 kv O/G Nangli line Load (Nangli,Mudiyanur, H.Gollahalli & Byrkur)shifted to T.Gollahalli Station,on 05.09.2021 now it is in idle condition.
LOSSES
[8 empty] | I/C to TRI+TRII | Maximum Voltage Date: -0.02%
| ASISTANT EXECUTIVE ENGINEER [ ELE] | [6 empty] | TRI to BANK I | Maximum Voltage Date: 1.849%; Minimum Voltage Time: ASISTANT ENGINEER [ MAINT ]
| Nodal officer-1 KPTCL, Kolar | [6 empty] | TRII to BANKII | Maximum Voltage Date: 0.5725%; Minimum Voltage Time: 66/11 KV MUSS, KPTCL.
[8 empty] | I/C to Banks | Maximum Voltage Date: 1.25% |  |  | KEMBODI
[32 empty] | 66 | 33:10 | 39 | 29:25 | 3 | 2:30 | 112 | 678:55
[32 empty] | 4 | 5:25 | 9 | 11:15 | 78 | 510:20 | 84 | 217:00
[32 empty] | 9 | 3:20 | 1 | 2:00 | 78 | 517:40 | 87 | 217:00
[32 empty] | 37 | 14:45 | 26 | 7:00 | 3 | 2:30 | 83 | 719:45

## VITAL PARAMETER KEM
Vital parameters for the sub station for the month of March-2025
Sub station: KEMBODI |  |  | TL&SS Division : KOLAR |  |  |  |  | Maint Circle: BRAZ |  |  |  |  | Transmission Zone : Bangalore
Sl No | Particulars | Capacity of Transformer/ feeder |  | Peak Demand in MW |  |  |  | Energy in MU |  | Voltage recorded in kV |  | Quantum of power supply in hours |  |  |  | Interruption |  |  |  | Loading factor (3a)/(2a) | Load factor (5b)/[3b)*24* No of days in a month /1000]
|  | in A | in MVA | Normal |  | Contingency |  | Entitlement for the month | Actual recording | Max | Min | Three phase |  | Open delta |  | Scheduled |  | Un scheduled
[12 empty] | Schd. | Act. | Schd. | Act. | Nos | Dur in hrs | Nos | Dur in hrs
|  |  |  | in A | in MW | in A | in MW
| 2 | 2a | 2b | 3a | 3b | 4a | 4b | 5a | 5b | 6 | 7 | 8a | 8b | 10a | 10b | 11 |  | 12 |  | 12 | 13
10.3704 | Sub-station | 840 | 16 | 864 | 14.4 |  |  |  | 0 | 66.9 | 63.5 | [8 empty] | 1.0286 | 0
11.1959 | [21 empty] | Un scheduled
12.0214 | Transformer-1 | 420 | 8 | 540 | 9 |  |  |  | 2.8772 | 11.8 | 10.7 | [8 empty] | 1.2857 | 0.23785 | Nos | Dur in hrs
12.8469 | Transformer-2 | 420 | 8 | 384 | 6.4 |  |  |  | 2.3719 | 11.8 | 0 | [8 empty] | 0.91429 | 0.27573
13.6724 | F1-Hutturu | 170 | 3.238 | 80 | 1.3333 |  |  |  | 0.42248 |  |  | 744 | 722:55 | 0 |  | 0 | 0:00 | 44 | 21:05 | 0.47059 | 0.23574 | F+Msf+Lc
14.4979 | F2-Abbani | 170 | 3.238 | 200 | 3.3333 |  |  |  | 0.57414 |  |  | 217 | 215:30 | 0 | 0:00 | 78 | 517:40 | 13 | 10:50 | 1.1765 | 0.12815
15.3234 | F3-Kembodi | 170 | 3.238 | 200 | 3.3333 |  |  |  | 0.66438 |  |  | 217 | 214:00 | 0 | 0:00 | 76 | 510:50 | 22 | 19:10 | 1.1765 | 0.14829
16.1488 | F-4 Holali(NJY) | 170 | 3.238 | 80 | 1.3333 |  |  |  | 0.59766 |  |  | 744 | 704:50 | 0 |  | 0 | 0:00 | 67 | 39:10 | 0.47059 | 0.33349
16.9743 | F-5 Lotus form | 170 | 3.238 | 170 | 2.8333 |  |  |  | 0.84192 |  |  | 744 | 723:45 | 0 |  | 0 | 0:00 | 53 | 20:15 | 1 | 0.22108
17.7998 | F6-Vitapnahalli | 170 | 3.238 | 200 | 3.3333 |  |  |  | 0.64006 |  |  | 217 | 217:00 | 0 | 0:00 | 76 | 519:25 | 6 | 7:35 | 1.1765 | 0.14286
18.6253 | F7-Sisandra(NJY) | 170 | 3.238 | 70 | 1.1667 |  |  |  | 0.30322 |  |  | 744 | 727:40 | 0 |  | 0 | 0:00 | 51 | 16:20 | 0.41176 | 0.19337
| F8-Ramasandra | 170 | 3.238 | 70 | 1.1667 |  |  |  | 0.30322 |  |  | 217 | 217:00 | 0 | 0:00 | 78 | 525:15 | 5 | 1:45 | 0.41176 | 0.19337
19.4508 | F9-Shapur | 170 | 3.238 | 200 | 3.3333 |  |  |  | 0.57442 |  |  | 217 | 217:00 | 0 | 0:00 | 77 | 512:55 | 12 | 527:00 | 1.1765 | 0.12821
Remarks
Duration of Maximum voltage beyond specified limits -- NIL
Duration of Minimum voltage beyond specified limits -- NIL
|  |  |  | Assistant Executive Engineer (Ele), | [12 empty] | Assistant Engineer (Ele),
|  |  |  | Kolar Nodal-1 | [11 empty] | 66/11KV MUSS
|  |  |  | KPTCL, KOLAR. | [12 empty] | KPTCL, Kembodi.

## Energy Audit
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
66/11 KV Substation Kembodi MONTHLY ENERGY AUDIT FOR THE MONTH OF March-2025
SL NO | EQUIPMENT | PRESENT | PREVIOUS | DIFF. | M.C. | CONSUMPTION
1 | 66KV I/C Line Kolar | 1073526 | 1070902 | 2624 | 2000 | 5248000
2 | 66 KV OG Line Nangli | 844622 | 844622 | 0 | 2000 | 0
| TOTAL |  |  |  |  | 5248000
5 | TRANSFORMER-1 | 170572.9 | 169134.3 | 1438.6 | 2000 | 2877200
6 | TRANSFORMER-2 | 242641 | 240269.1 | 2371.9 | 1000 | 2371900
TOTAL | [5 empty] | 5249100
7 | BANK-1 | 145.973 | 110.673 | 35.3 | 80000 | 2824000
| BANK-1(Import) | 0 | 0 | 0 | 80000 | 0
| BANK-1 (Total) |  |  |  |  | 2824000
8 | BANK-2 | 1109.129 | 1079.65 | 29.479 | 80000 | 2358320
TOTAL | [5 empty] | 5182320
9 | F 1 - Huttur | 2046.477 | 2025.353 | 21.124 | 20000 | 422480
10 | F 2 - Abbani | 1136.413 | 1107.706 | 28.707 | 20000 | 574140
11 | F 3 - Kembodi | 890.404 | 857.185 | 33.219 | 20000 | 664380
12 | F 4 - Holali | 137.114 | 107.231 | 29.883 | 20000 | 597660
| F 4 - Holali (Import) | 0 | 0 | 0 | 20000 | 0
13 | F-9 Shapur | 994.012 | 966.459 | 27.553 | 20000 | 551060
TOTAL | [5 empty] | 2809720
14 | F5 - Lotus | 1225.759 | 1183.663 | 42.096 | 20000 | 841920
15 | F6 - Vittapanahalli | 1132.932 | 1100.929 | 32.003 | 20000 | 640060
16 | F7 - Seesandra | 1011.801 | 996.64 | 15.161 | 20000 | 303220
17 | F8 - Ramasandra | 40.377 | 11.656 | 28.721 | 20000 | 574420
TOTAL | [5 empty] | 2359620
|  |  | FEEDERS TOTAL |  |  | 5169340
SL NO | NAME OF THE LINE/EQPT |  |  |  | % LOSSES
1 | LINE TO TRANSFORMERS |  |  |  | -0.02096%
2 | TRANSFORMER-1 TO BANK-1 |  |  |  | 1.849%
3 | TRANSFORMER-2 TO BANK-2 |  |  |  | 0.5725%
4 | BANK-1 TO FEEDERS |  |  |  | 0.5057%
5 | BANK-2 TO FEEDERS |  |  |  | -0.05512%
6 | TRF TO BANKS |  |  |  | 1.272%
7 | LINE TO BANKS |  |  |  | 1.252%
Asst. Executive Engineer (Ele) |  |  |  |  | Assistant Engineer (Ele)
Nodal Officer-1, KPTCL |  |  |  |  | 66/11KV Sub-Station
220KV R/S, KOLAR |  |  |  |  | Kembodi

## Max-Min
MAXIMUM AND MINIMUM VOLTAGE OF STATION BUS RECORDED DURING month of March-2025 Kembodi IN TRANSMISSION ZONE,BRAZ
SL NO | DIVISION | STATION NAME | VTG CLASS(220/66/11KV ) | HV SIDE | [5 empty] | LV1 SIDE | [5 empty] | LV2 SIDE
|  |  |  | MAX VTG | DATE | TIME | MIN VTG | DATE | TIME | MAX VTG | DATE | TIME | MIN VTG | DATE | TIME | MAX VTG | DATE | TIME | MIN VTG | DATE | TIME
1 | KOLAR | Kembodi
|  |  |  | 66.9 | 01.03.2025 | 16:00 | 63.5 | 21.03.2025 | 6:00 | 11.8 | 01.03.2025 | 16:00 | 10.7 | 06.03.2025 | 5:00 | 11.8 | 01.03.2025 | 11:00 | 10.7 | 06.03.2025 | 5:00

## 66kv
STATEMENT SHOWING THE DETAILS OF TRANSMISSION ELEMENT OUTAGES FOR THE MONTH OF March-2025
66/11KV MUSS Kembodi KPTCL
Sl. No | Date | Line/ Eqpt. | Scheduled |  |  | Unscheduled |  |  | Remarks
|  |  | From | To | Duration | From | To | Duration
1 |  | Incoming & O/G | [6 empty] | Nill
TR-1 , INTERRUPTIONS
Sl. No | Date | Line/ Eqpt. | Scheduled |  |  | Unscheduled |  |  | Remarks
|  |  | From | To | Duration | From | To | Duration
1 |  | Transformer-1 12.5 MVA |  |  |  | 14:25 | 15:40 | 1:15 | Availed LC for replacement of burnt out Bank-1 Y phase female contact.
TR-2 , INTERRUPTIONS
Sl. No | Date | Line/ Eqpt. | Scheduled |  |  | Unscheduled |  |  | Remarks
|  |  | From | To | Duration | From | To | Duration
1 |  | Tr-2 8 MVA | [6 empty] | Nill
Assistant Executive Engineer(Ele.) | [7 empty] | Assistant Engineer Ele
& Nodal Officer-1, KPTCL | [7 empty] | 66/11 KV MUSS KPTCL
220KV R/S, KOLAR | [7 empty] | Kembodi

## condition mon
Condition Monitoring of station equipments for the Month of March-2025
Sl. No | Name of the Station | Name of the Equipments | Maintenanace done yes /No | Date of recent maintenanance
1 | 66/11KV S/S Kembodi | 220KV Power Transformers
2 |  | 66KV Power Transformers | Yes | 21.3.2025
3 |  | Current Transformers | Yes | 21.3.2025
4 |  | Induction type Potential Transformers
5 |  | Circuit Breakers
6 |  | 11 KV Switchgear
7 |  | MCVCB
8 |  | PCVCB | Yes
9 |  | Lightening Arresters
10 |  | Isolators
11 |  | Line Isolators
12 |  | Earth Isolators
13 |  | Battery Sets | Yes | 3/03,10/03,17/03,24/03, & 31/3/2025
14 |  | Battery charger | Yes | 01.03.2025
15 |  | Capacitor Banks
16 |  | Other maintenanace | Yes | 21.03.2025 & 29.03.2025

## Sheet1
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
FEEDERS DETAILS OF 66/11 KV MUSS KEMBODI, KPTCL , TL&SS DIVISION , KPTCL, KOLAR
FEEDER NO | FEEDERS NAME | TYPE OF FEEDER | PEAK LOAD |  | 3 PH |  | TOTAL 3 PH | OPEN DELTA | DURATION | LS | DURATION
|  |  | AMPS | MWs | DAY | NIGHT
F1 | Hutturu | NJY | 0 | 1.8 |  |  | 24 Hrs | 0
F2 | Abbani | AGRI | 0 | 0 | 9:00 - 13:00 | 23:00-02:00 | 7Hrs | 18.00-2.00 | 8Hrs | 6.00-9:00 /13:00-18.00 | 9HRS
F3 | Kembodi | AGRI | 200 | 3.3333 | 13:00- 17:00 | 02:00-05:00 | 7Hrs | 18.00-22.00 | 8Hrs | 6.00-10.30/13.30-18.00 | 9HRS
F4 | Holali | NJY | 80 | 1.3333 | OO.OO | 24 | 24 Hrs | 0 |  | 0
F5 | Lotus | NJY | 170 | 2.8333 | OO.OO | 24 | 24 Hrs | 0 |  | 0
F6 | Vittapanahalli | AGRI | 200 | 3.3333 | 9:00 - 13:00 | 02:00-05:00 | 7Hrs | 18.00-22.00 | 8Hrs | 6.00-10.30/13.30-18.00 | 9HRS
F7 | Seesandra | NJY | 70 | 1.1667 | OO.OO | 24 | 24 Hrs | 0 |  | 0
F8 | Ramasandra | AGRI | 200 | 3.3333 | 13:00- 17:00 | 23:00-02:00 | 7Hrs | 18.00-2.00 | 8Hrs | 6.00-13.30 /16.30-18.00 | 9HRS
F9 | Shapur | AGRI | 190 | 3.1 | 11:00-15:00 | 23:00-02:00
NOTE | TOTAL CAPACITY - 1X12.5 MVA & 1X8MVA
TOTAL NJY FEEDERS -04
TOTAL IDLE FEEDERS- 0
TOTAL AGRI FEEDERS - 5
TOTAL IND FEEDERS - 0
ASISTANT ENGINEER [ MAINT ]
ASISTANT EXECUTIVE ENGINEER [ ELE] | [8 empty] | 66/11 KV MUSS, KPTCL.
TL AND SS DIVISSION, KPTCL | [8 empty] | KEMBODI
KOLAR

## major equip
Proforma for details of equipment failure March-2025 ( Information should be in detail and test reports should be furnished)
1 | Name of substation | 66/11kV MUSS Kembodi
2 | Utility/Owner of substation | KPTCL
3 | Faulty Equipment | Nill
4 | Rating | Nill
5 | Make | Nill
6 | Sr No | Nill
7 | Year of manufacturing | Nill
8 | Year of commissioning | Nill
9 | Date and time of occurrence/discovery of fault | Nill
10 | Fauilt discvered during | Nill
11 | Present condtion of equipment | Nill
12 | Details of previous maintenance | Nill
13 | Details of previous failure | Nill
14 | Sequence of events/Description of fault | Nill
15 | Details of tests done after failure | Nill
16 | Conclusion/recommendations | Nill
Aaaistant Engineer(Ele)
66/11KV MUSS
KPTCL, Kembodi

## work report
MONTHLY WORKS REPORT OF BRAZ CIRCLE for March-2025
TABLE-A Details regarding the newly commissioned Transformers or Equiments /Erection or Installation/APW/ GCW works carried out in various stations of BRAZ Circle
Sl.No | Name of the Division | Name of the Station | Name of the work | Voltage Class | Nomenclature of the Equipment | Make , Serial No. and Specifications | Date of Commission/ Erection | Remarks if any
| TL & SS Division Kolar | 66/11kV MUSS Kembodi | Nill |  | Nill |  |  | Nill
TABLE-B Details regarding replacement works in existing equipments carried out in various stations of BRAZ Circle
Sl.No
1 | Name of the Division | Name of the Station | Name of the work | Voltage Class | Nomenclature of the Equipment | Make , Serial No. and Specifications | Date of Replacement / Erection | Remarks if any
| TL & SS Division Kolar | 66/11kV MUSS Kembodi | ….. |  |  |  |  | …..
Note: Please furnish the above sought details of the works carried out within 5 th of every month without fail ,in future.