## Feederwise Energy Audit (9 (12
Feeder to Consumer Audit Nov-2024 INPUT and Dec-2024 DCB)
SL. No. | AREA- RAPDRP/Non_RAPDRP/sharing between RAPDRP & Non_RAPDRP | Sub Division | O&M Section | STATION | FEEDER NO.& NAME (as per MDM) |  | FEEDER CODE (as per MDM) | Feeder Type CATEGORY-Urban/ Rural/ Industrial/ Commercial/ Domestic/ NJY/ AGRI/ Mixed Load/ Water works/ others | Length of the Feeder in Km |  |  | Total No of DTCs on Feeder | Total Installation Counts |  | FEEDER METER READING DETAILS | [6 empty] | CORRECTION FACTOR | FEEDER CONSUMPTION WITH CF IN UNITS | BOUNDARY METER READING DETAILS | [11 empty] | 11 KV Wheeled Energy in Units | 11KV OPEN ACCESS Consumption in Units (Input) | SRTPV (Net Metering + Gross Metering) | TOTAL INPUT ENERGY (FEEDER CONSUMPTION + IMPORT-EXPORT+SRTPV) in Units |  |  | 11KV OPEN ACCESS Consumption in Units (Sales) (It should not be added in the metered sales) | 11KV Wheeled Energy in Units (Sales) (It should not be added in the metered sales) | BILLED CONSUMPTION (Metered Sales) in Units | Unmetered consumption (LT4a/ SL/ WS) in Units | TOTAL ENERGY SALES in Units | Energy Loss in Units | %feeder Loss |  |  | T&D Loss Range | %Billing Efficiency | % BE with Assessed Sales | OB | Demand In Rs | Collection In Rs | CB | % Collection Efficiency | %AT&C loss | % AT & C LOSS with BE assessed | AT&C Loss Range-1 | Collection Efficiency restricted to 100% | % AT & C LOSS CE restricted to 100% | AT&C Loss Range-2 | Assessed Sales in Units | TOTAL Sales after assessment | Anaylized Feeder loss after assessing the energy | T&D Loss Range after assessment | Remarks (Assessed Energy/ Import/ Export/Others) | REMARKS & Reasons for -ve, above 10% for T & D LOSS | REMARKS & Reasons for-ve above 10% for AT&C LOSS | Action Plan for reducing the T&D LOSS | Methodology adopted to achieve T&Dloss below 3% | REMARKS & Reasons for-ve above 10% for AT&C LOSS
[15 empty] | FR | IR |  |  | DIFF | METER CONSTANT | FEEDER CONSUMPTION IN UNITS |  |  | IMPORT |  |  |  | Import (Change over feeder/ Assessed where no boundary meter) | TOTAL IMPORT IN UNITS | EXPORT |  |  |  | Export (Change over feerder/Accessd where no boundary meter) | TOTAL EXPORT IN UNITS
[9 empty] | Trunk Line | Spur Line | Total Length |  | Other than LT4a | LT4a | [9 empty] | FR | IR | DIFF | CONSTANT |  |  | FR | IR | DIFF | CONSTANT | [15 empty] | EA FORMATE FEEDER LOSS | DIFFERENCE
1 | 1a | 2 | 3 | 4 | 5 |  | 6 | 7 | 7a | 7b | 7c | 8 | 9 | 10 | 11 | 12 |  |  | 13=11-12 | 14 | 15=13*14 | 16 | 17 | 18 | 19 | 20=18-19 | A | B | 21=(20*A)+B | 22 | 23 | 24=22-23 | C | D | 25=(24*C)+D | 26 | 27 | 28 | 29=17+21-25+28 |  |  | 30 | 31 | 32 | 33 | 34=30+31+ 32+33 | 35=29-34 | 36=35/29*100 |  |  |  | 37=34/29*100 | 38=49/29*100 | 38 | 39 | 40 | 41 | 42=40/39*100 | 43=(1-(37*42)/ 10000)*100 | 45=((1-38*43/10000))*100 |  | 46 | 47=((1-38*46/10000))*100 |  | 44 | 45=34+44 | 46 |  | 47 | 48 |  |  | 49
1 | Non_RAPDRP | HIRIYUR | O&M-2 | BHARAMAGIRI_66 | F01-KUBARAHALLY | BHARAMAGIRI_66F01-KUBARAHALLY | 1310401910010101 | AGRI | 14.875 | 13.972 | 28.847 | 118 | 29 | 281 | 71.047 | 49.404 | 49.404 | 0 | 21.643 | 20000 | 432860 | 1 | 432860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432860 |  |  | 0 | 0 | 391737.431 | 0 | 391737.431 | 41122.569 | 9.5002 | 9.5 | 0.00020076 | 5-10 | 90.4998 | 90.4998 | 7388875 | 2279912.11 | 2279911.716 | 7388875.01 | 100 | 9.5002 | 9.5002 | 5-10 | 100 | 9.5002 | 5-10 |  | 391737.431 | 9.5002 | 5-10
2 | Non_RAPDRP | HIRIYUR | O&M-2 | BHARAMAGIRI_66 | F03-NJYMARIKANUVE | BHARAMAGIRI_66F03-NJYMARIKANUVE | 1310401910010102 | NJY | 18.8822 | 21.008 | 39.8902 | 42 | 2209 | 0 | 428.518 | 428.518 | 428.518 | 0 | 0 | 20000 | 86938 | 1 | 86938 | 0 | 0 | 0 | 0 | 52000 | 52000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138938 |  |  | 0 | 0 | 127573.05 | 0 | 127573.05 | 11364.95 | 8.1799 | 8.18 | -0.0001284 | 5-10 | 91.8201 | 91.8201 | 10229038.72 | 1362431.75 | 1078255.75 | 10513214.72 | 79.142 | 27.3317 | 27.3317 | 20-30 | 79.142 | 27.3317 | 20-30 |  | 127573.05 | 8.1799 | 5-10
3 | Non_RAPDRP | HIRIYUR | O&M-2 | BHARAMAGIRI_66 | F04-V.V.PURA | BHARAMAGIRI_66F04-V.V.PURA | 1310401910010103 | AGRI | 18.7688 | 17.64 | 36.4088 | 148 | 1 | 336 | 772.991 | 754.654 | 754.654 | 0 | 18.337 | 20000 | 366740 | 1 | 366740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366740 |  |  | 0 | 0 | 331900.456 | 0 | 331900.456 | 34839.544 | 9.4998 | 9.5 | -0.00020614 | 5-10 | 90.5002 | 90.5002 | 12086759 | 1932917.42 | 1931660.424 | 12088017 | 99.935 | 9.5586 | 9.5586 | 5-10 | 99.935 | 9.5586 | 5-10 |  | 331900.456 | 9.4998 | 5-10
4 | Non_RAPDRP | HIRIYUR | O&M-2 | BHARAMAGIRI_66 | F05-A.V.KOTTEGE | BHARAMAGIRI_66F05-A.V.KOTTEGE | 1310401910020301 | AGRI | 22.5626 | 21.208 | 43.7706 | 88 | 1 | 354 | 785.441 | 756.327 | 756.327 | 0 | 29.114 | 20000 | 582280 | 1 | 582280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582280 |  |  | 0 | 0 | 526964.088 | 0 | 526964.088 | 55315.912 | 9.4999 | 9.5 | -0.00011816 | 5-10 | 90.5001 | 90.5001 | 10994331.18 | 3067089.97 | 3066988.645 | 10994432.21 | 99.9967 | 9.5029 | 9.5029 | 5-10 | 99.9967 | 9.5029 | 5-10 |  | 526964.088 | 9.4999 | 5-10
5 | Non_RAPDRP | HIRIYUR | O&M-2 | BHARAMAGIRI_66 | F06-GOGUDDU | BHARAMAGIRI_66F06-GOGUDDU | 1310401910020302 | AGRI | 15.205 | 14.3072 | 29.5122 | 112 | 39 | 255 | 72.84 | 46.277 | 46.277 | 0 | 26.563 | 20000 | 531260 | 1 | 531260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531260 |  |  | 0 | 0 | 457101 | 0 | 457101 | 74159 | 13.9591 | 13.96 | -0.00092158 | 10-15 | 86.0409 | 86.0409 | 6880233.77 | 2660448.74 | 2660448.74 | 6880233.77 | 100 | 13.9591 | 13.9591 | 10-15 | 100 | 13.9591 | 10-15 |  | 457101 | 13.9591 | 10-15
6 | Non_RAPDRP | HIRIYUR | O&M-2 | BHARAMAGIRI_66 | F07-BHOOTHAYANAHATTI | BHARAMAGIRI_66F07-BHOOTHAYANAHATTI | 1310401910020303 | AGRI | 15.375 | 14.472 | 29.847 | 118 | 2 | 428 | 1248.701 | 1198.842 | 1198.842 | 0 | 49.859 | 20000 | 997180 | 1 | 997180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 120000 | 0 | 0 | 0 | 877180 |  |  | 0 | 0 | 762200 | 0 | 762200 | 114980 | 13.1079 | 13.11 | -0.002086 | 10-15 | 86.8921 | 86.8921 | 13965711 | 4436004 | 4436004 | 13965711 | 100 | 13.1079 | 13.1079 | 10-15 | 100 | 13.1079 | 10-15 |  | 762200 | 13.1079 | 10-15
7 | Non_RAPDRP | HIRIYUR | O&M-2 | BHARAMAGIRI_66 | F08-NJYBHARAMAGIRI | BHARAMAGIRI_66F08-NJYBHARAMAGIRI | 1310401910020304 | NJY | 19.1688 | 18.04 | 37.2088 | 47 | 1646 | 0 | 260.088 | 255.849 | 255.849 | 0 | 4.239 | 20000 | 84780 | 1 | 84780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11000 | 11000 | 0 | 0 | 0 | 73780 |  |  | 0 | 0 | 65199.2 | 0 | 65199.2 | 8580.8 | 11.6303 | 11.63 | 0.0002521 | 10-15 | 88.3697 | 88.3697 | 11196165.54 | 779721.28 | 390613.28 | 11585273.54 | 50.0965 | 55.7298 | 55.7298 | >30 | 50.0965 | 55.7298 | >30 |  | 65199.2 | 11.6303 | 10-15
8 | Non_RAPDRP | HIRIYUR | O&M-2 | BHARAMAGIRI_66 | F09- VVS WATER SUPPLY | BHARAMAGIRI_66F09- VVS WATER SUPPLY | 1310401910010104 | WATER WORKS | 3.225 | 0.8 | 4.025 | 1 | 2 | 0 | 1197.008 | 1170.727 | #N/A | #N/A | 26.281 | 10000 | 262810 | 1 | 262810 | 0 | 0 | 0 | 0 | 20000 | 20000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282810 |  |  | 0 | 0 | 254950 | 0 | 254950 | 27860 | 9.8511 | 9.85 | 0.0011368 | 5-10 | 90.1489 | 90.1489 | 8911675 | 2201264 | 1434884 | 9678055 | 65.1845 | 41.2369 | 41.2369 | >30 | 65.1845 | 41.2369 | >30 |  | 254950 | 9.8511 | 5-10
9 | Non_RAPDRP | HIRIYUR | O&M-2 | BHARAMAGIRI_66 | F11-KUNIKERE KAVALU | BHARAMAGIRI_66F11-KUNIKERE KAVALU | 1310401910010105 | AGRI | 15.675 | 14.772 | 30.447 | 118 | 29 | 356 | 529.615 | 503.532 | 503.532 | 0 | 26.083 | 20000 | 521660 | 1 | 521660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521660 |  |  | 0 | 0 | 472103.464 | 0 | 472103.464 | 49556.536 | 9.4998 | 9.5 | -0.00022313 | 5-10 | 90.5002 | 90.5002 | 16457301 | 2747931.13 | 2747601.403 | 16457631 | 99.988 | 9.5106 | 9.5106 | 5-10 | 99.988 | 9.5106 | 5-10 |  | 472103.464 | 9.4998 | 5-10
10 | Non_RAPDRP | HIRIYUR | O&M-2 | BHARAMAGIRI_66 | F12-TALAVARAHATTY | BHARAMAGIRI_66F12-TALAVARAHATTY | 1310401910010107 | AGRI | 20.5657 | 19.324 | 39.8897 | 88 | 0 | 234 | 1640.83 | 1442.9 | 1442.9 | 0 | 197.93 | 2000 | 395860 | 1 | 395860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395860 |  |  | 0 | 0 | 344500 | 0 | 344500 | 51360 | 12.9743 | 12.97 | 0.0042838 | 10-15 | 87.0257 | 87.0257 | 5177030 | 2004990 | 2004990 | 5177030 | 100 | 12.9743 | 12.9743 | 10-15 | 100 | 12.9743 | 10-15 |  | 344500 | 12.9743 | 10-15
11 | Non_RAPDRP | HIRIYUR | O&M-2 | BHARAMAGIRI_66 | F13-Y.N.HAALY | BHARAMAGIRI_66F13-Y.N.HAALY | 1310401910010108 | AGRI | 22.4226 | 21.068 | 43.4906 | 121 | 0 | 214 | 1450.51 | 1278.76 | 1278.76 | 0 | 171.75 | 2000 | 343500 | 1 | 343500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343500 |  |  | 0 | 0 | 303900 | 0 | 303900 | 39600 | 11.5284 | 11.53 | -0.0016157 | 10-15 | 88.4716 | 88.4716 | 3816406 | 1768698 | 1768698 | 3816406 | 100 | 11.5284 | 11.5284 | 10-15 | 100 | 11.5284 | 10-15 |  | 303900 | 11.5284 | 10-15
12 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F02-CHILLAHALLY | HARIYABBE_66F02-CHILLAHALLY | 1310401906010101 | AGRI | 23.1686 | 21.888 | 45.0566 | 102 | 19 | 477 | 928.82 | 899.08 | 899.08 | 0 | 29.74 | 20000 | 594800 | 1 | 594800 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604800 |  |  | 0 | 0 | 547346.022 | 0 | 547346.022 | 57453.978 | 9.4997 | 9.5 | -0.00033433 | 5-10 | 90.5003 | 90.5003 | 22424447.59 | 3185719.58 | 3185596.506 | 22424569.57 | 99.9961 | 9.5032 | 9.5032 | 5-10 | 99.9961 | 9.5032 | 5-10 |  | 547346.022 | 9.4997 | 5-10
13 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F01-GULYA | HARIYABBE_66F01-GULYA | 1310401906010108 | AGRI | 23.2626 | 21.908 | 45.1706 | 112 | 0 | 275 | 718.33 | 681.78 | 681.78 | 0 | 36.55 | 20000 | 731000 | 1 | 731000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165000 | 165000 | 0 | 0 | 0 | 566000 |  |  | 0 | 0 | 489000 | 0 | 489000 | 77000 | 13.6042 | 13.6 | 0.0042403 | 10-15 | 86.3958 | 86.3958 | 13240417 | 2845980 | 2845980 | 13240417 | 100 | 13.6042 | 13.6042 | 10-15 | 100 | 13.6042 | 10-15 |  | 489000 | 13.6042 | 10-15
14 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F04-DHARMAPURA | HARIYABBE_66F04-DHARMAPURA | 1310401906010102 | AGRI | 13.4123 | 17.43 | 30.8423 | 123 | 85 | 1245 | 1167.38 | 1137.64 | 1137.64 | 0 | 29.74 | 20000 | 594800 | 1 | 594800 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604800 |  |  | 0 | 0 | 547344.894 | 0 | 547344.894 | 57455.106 | 9.4999 | 9.5 | -0.00014782 | 5-10 | 90.5001 | 90.5001 | 20944650 | 3189059.6 | 3185264.499 | 20948443.48 | 99.881 | 9.6076 | 9.6076 | 5-10 | 99.881 | 9.6076 | 5-10 |  | 547344.894 | 9.4999 | 5-10
15 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F05-SUGUR | HARIYABBE_66F05-SUGUR | 1310401906020301 | AGRI | 24.1394 | 23.842 | 47.9814 | 98 | 3 | 356 | 1092.04 | 1057.15 | 1057.15 | 0 | 34.89 | 20000 | 697800 | 1 | 697800 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 707800 |  |  | 0 | 0 | 636180 | 0 | 636180 | 71620 | 10.1187 | 10.12 | -0.0013224 | 10-15 | 89.8813 | 89.8813 | 4597850.78 | 3703213.71 | 3703213.71 | 4597850.78 | 100 | 10.1187 | 10.1187 | 10-15 | 100 | 10.1187 | 10-15 |  | 636180 | 10.1187 | 10-15
16 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F06-HOSAKERE | HARIYABBE_66F06-HOSAKERE | 1310401906020302 | AGRI | 25.9963 | 25.676 | 51.6723 | 104 | 326 | 376 | 993.45 | 962.78 | 962.78 | 0 | 30.67 | 20000 | 613400 | 1 | 613400 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623400 |  |  | 0 | 0 | 565288.895 | 0 | 565288.895 | 58111.105 | 9.3216 | 9.32 | 0.0016402 | 5-10 | 90.6784 | 90.6784 | 19596315.26 | 3300994.47 | 3289336.155 | 19607973.26 | 99.6468 | 9.6419 | 9.6419 | 5-10 | 99.6468 | 9.6419 | 5-10 |  | 565288.895 | 9.3216 | 5-10
17 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F07-HOOVINAHOLE | HARIYABBE_66F07-HOOVINAHOLE | 1310401906030501 | AGRI | 22.3126 | 24.53 | 46.8426 | 109 | 2 | 437 | 851.48 | 824.64 | 824.64 | 0 | 26.84 | 30000 | 805200 | 1 | 805200 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 815200 |  |  | 0 | 0 | 737755.666 | 0 | 737755.666 | 77444.334 | 9.5 | 9.5 | 4.0972e-05 | 5-10 | 90.5 | 90.5 | 10686182.51 | 4293903.8 | 4293899.454 | 10686187.51 | 99.9999 | 9.5001 | 9.5001 | 5-10 | 99.9999 | 9.5001 | 5-10 |  | 737755.666 | 9.5 | 5-10
18 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F08-SAKKARA | HARIYABBE_66F08-SAKKARA | 1310401906030502 | AGRI | 24.1694 | 22.702 | 46.8714 | 121 | 80 | 371 | 887.89 | 862.25 | 862.25 | 0 | 25.64 | 20000 | 512800 | 1 | 512800 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522800 |  |  | 0 | 0 | 473135.549 | 0 | 473135.549 | 49664.451 | 9.4997 | 9.5 | -0.00029629 | 5-10 | 90.5003 | 90.5003 | 3345369.64 | 2753784.27 | 2754083.403 | 3345070.64 | 100.0109 | 9.4899 | 9.4899 | 5-10 | 100 | 9.4997 | 5-10 |  | 473135.549 | 9.4997 | 5-10
19 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F09-NJY B.K.HATTY | HARIYABBE_66F09-NJY B.K.HATTY | 1310401906030503 | NJY | 18.8522 | 22.53 | 41.3822 | 44 | 5131 | 0 | 1288.88 | 1257.41 | 1257.41 | 0 | 31.47 | 10000 | 314700 | 1 | 314700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 35000 | 0 | 0 | 0 | 279700 |  |  | 0 | 0 | 248201 | 0 | 248201 | 31499 | 11.2617 | 11.26 | 0.001709 | 10-15 | 88.7383 | 88.7383 | 35168218.97 | 2787620.7 | 1751416.26 | 36204423.41 | 62.8284 | 44.2472 | 44.2472 | >30 | 62.8284 | 44.2472 | >30 |  | 248201 | 11.2617 | 10-15
20 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F10-KANDENAHALLI | HARIYABBE_66F10-KANDENAHALLI | 1310401906030504 | AGRI | 16.2723 | 26.19 | 42.4623 | 98 | 1 | 373 | 676.87 | 648.48 | 648.48 | 0 | 28.39 | 20000 | 567800 | 1 | 567800 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577800 |  |  | 0 | 0 | 522908.1 | 0 | 522908.1 | 54891.9 | 9.5002 | 9.5 | 0.00015576 | 5-10 | 90.4998 | 90.4998 | 16836716 | 3043325.92 | 3043325.263 | 16836716 | 100 | 9.5002 | 9.5002 | 5-10 | 100 | 9.5002 | 5-10 |  | 522908.1 | 9.5002 | 5-10
21 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F11-ESHWARAGERE | HARIYABBE_66F11-ESHWARAGERE | 1310401906010103 | NJY | 27.8932 | 26.2 | 54.0932 | 42 | 2513 | 0 | 1517.68 | 1486.66 | 1486.66 | 0 | 31.02 | 10000 | 310200 | 1 | 310200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192000 | 192000 | 0 | 0 | 0 | 118200 |  |  | 0 | 0 | 105483.55 | 0 | 105483.55 | 12716.45 | 10.7584 | 10.76 | -0.0015821 | 10-15 | 89.2416 | 89.2416 | 41923297.96 | 1454862.88 | 1015938.68 | 42362222.16 | 69.8305 | 37.6821 | 37.6821 | >30 | 69.8305 | 37.6821 | >30 |  | 105483.55 | 10.7584 | 10-15
22 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F12-NJY HOSAHALLY | HARIYABBE_66F12-NJY HOSAHALLY | 1310401906010104 | NJY | 18.6688 | 17.54 | 36.2088 | 46 | 1847 | 0 | 819.32 | 805.06 | 805.06 | 0 | 14.26 | 10000 | 142600 | 1 | 142600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 75000 | 0 | 0 | 0 | 67600 |  |  | 0 | 0 | 59150 | 0 | 59150 | 8450 | 12.5 | 12.5 | 1.3571e-12 | 10-15 | 87.5 | 87.5 | 26411630.2 | 767932.02 | 524629.02 | 26654933.2 | 68.3171 | 40.2225 | 40.2225 | >30 | 68.3171 | 40.2225 | >30 | 0 | 59150 | 12.5 | 10-15
23 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F13-KHANAJANAHALLY NJY | HARIYABBE_66F13-KHANAJANAHALLY NJY | 1310401906020303 | NJY | 22.3726 | 21.018 | 43.3906 | 39 | 1373 | 0 | 616.8 | 603.64 | 603.64 | 0 | 13.16 | 10000 | 131600 | 1 | 131600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72000 | 72000 | 0 | 0 | 0 | 59600 |  |  | 0 | 0 | 53883.5 | 0 | 53883.5 | 5716.5 | 9.5914 | 9.59 | 0.001443 | 5-10 | 90.4086 | 90.4086 | 17688150.56 | 681669.53 | 467141.53 | 17902678.56 | 68.529 | 38.0439 | 38.0439 | >30 | 68.529 | 38.0439 | >30 |  | 53883.5 | 9.5914 | 5-10
24 | Non_RAPDRP | HIRIYUR | HARIYABBE | HARIYABBE_66 | F03-V.K.GUDDA | HARIYABBE_66F03-V.K.GUDDA | 1310401906010107 | AGRI | 19.5 | 20.56 | 40.06 | 122 | 4 | 296 | 45 | 18.48 | 470.64 | -452.16 | 26.52 | 20000 | 530400 | 1 | 530400 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540400 |  |  | 0 | 0 | 489062.115 | 0 | 489062.115 | 51337.885 | 9.5 | 9.5 | -2.1281e-05 | 5-10 | 90.5 | 90.5 | 4054530.69 | 2846951.25 | 2846484.311 | 4054997.69 | 99.9836 | 9.5148 | 9.5148 | 5-10 | 99.9836 | 9.5148 | 5-10 |  | 489062.115 | 9.5 | 5-10
25 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F01-YELLADAKERE | HINDASGHATTA_66F01-YELLADAKERE | 1310401904010101 | AGRI | 19.352 | 22.35 | 41.702 | 98 | 48 | 288 | 648.667 | 623.522 | 623.522 | 0 | 25.145 | 20000 | 502900 | 1 | 502900 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512900 |  |  | 0 | 0 | 464173.28 | 0 | 464173.28 | 48726.72 | 9.5002 | 9.5 | 0.00023786 | 5-10 | 90.4998 | 90.4998 | 4817073.34 | 2708928.22 | 2705421.501 | 4820580.34 | 99.8705 | 9.6174 | 9.6174 | 5-10 | 99.8705 | 9.6174 | 5-10 |  | 464173.28 | 9.5002 | 5-10
26 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F02-MAVINAMADU | HINDASGHATTA_66F02-MAVINAMADU | 1310401904010102 | AGRI | 17.98 | 23.56 | 41.54 | 112 | 4 | 435 | 851.633 | 823.415 | 823.415 | 0 | 28.218 | 20000 | 564360 | 1 | 564360 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574360 |  |  | 0 | 0 | 519796.998 | 0 | 519796.998 | 54563.002 | 9.4998 | 9.5 | -0.00020858 | 5-10 | 90.5002 | 90.5002 | 9301374 | 3026328.56 | 3024345.59 | 9303357 | 99.9345 | 9.5591 | 9.5591 | 5-10 | 99.9345 | 9.5591 | 5-10 |  | 519796.998 | 9.4998 | 5-10
27 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F03-RANGAPURA | HINDASGHATTA_66F03-RANGAPURA | 1310401904010103 | AGRI | 20.5657 | 19.324 | 39.8897 | 88 | 4 | 480 | 781.281 | 755.893 | 755.893 | 0 | 25.388 | 20000 | 507760 | 1 | 507760 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 517760 |  |  | 0 | 0 | 468573.71 | 0 | 468573.71 | 49186.29 | 9.4998 | 9.5 | -0.00017576 | 5-10 | 90.5002 | 90.5002 | 13750738 | 2727285.22 | 2727104.49 | 13750919 | 99.9934 | 9.5058 | 9.5058 | 5-10 | 99.9934 | 9.5058 | 5-10 |  | 468573.71 | 9.4998 | 5-10
28 | Non_RAPDRP | HIRIYUR | DINDAWARA/O&M2 | HINDASGHATTA_66 | F04-SOMERAHALLY | HINDASGHATTA_66F04-SOMERAHALLY | 1310401904010104 | AGRI | 22.4226 | 21.068 | 43.4906 | 121 | 11 | 530 | 4373.1 | 4137.93 | 4137.93 | 0 | 235.17 | 2000 | 470340 | 1 | 470340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470340 |  |  | 0 | 0 | 425656.935 | 0 | 425656.935 | 44683.065 | 9.5002 | 9.5 | 0.00016265 | 5-10 | 90.4998 | 90.4998 | 17621793 | 2477496.16 | 2477535.742 | 17621754 | 100.0016 | 9.4987 | 9.4987 | 5-10 | 100 | 9.5002 | 5-10 |  | 425656.935 | 9.5002 | 5-10
29 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F05-ARISHINAGUNDI | HINDASGHATTA_66F05-ARISHINAGUNDI | 1310401904020301 | AGRI | 18.7388 | 17.61 | 36.3488 | 68 | 1 | 396 | 932.253 | 903.357 | 903.357 | 0 | 28.896 | 30000 | 866880 | 1 | 866880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 85000 | 0 | 0 | 0 | 781880 |  |  | 0 | 0 | 707600.849 | 0 | 707600.849 | 74279.151 | 9.5001 | 9.5 | 7.0471e-05 | 5-10 | 90.4999 | 90.4999 | 5931403.28 | 4118396.68 | 4118392.718 | 5931408.22 | 99.9999 | 9.5002 | 9.5002 | 5-10 | 99.9999 | 9.5002 | 5-10 |  | 707600.849 | 9.5001 | 5-10
30 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F06-V.V.PURA | HINDASGHATTA_66F06-V.V.PURA | 1310401904020302 | AGRI | 13.2082 | 12.418 | 25.6262 | 98 | 12 | 317 | 770.831 | 752.001 | 752.001 | 0 | 18.83 | 20000 | 376600 | 1 | 376600 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386600 |  |  | 0 | 0 | 349871.94 | 0 | 349871.94 | 36728.06 | 9.5003 | 9.5 | 0.00027419 | 5-10 | 90.4997 | 90.4997 | 6262094.73 | 2036774.95 | 2036349.71 | 6262518.73 | 99.9791 | 9.5192 | 9.5192 | 5-10 | 99.9791 | 9.5192 | 5-10 |  | 349871.94 | 9.5003 | 5-10
31 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F07-S.L.RSTEELS | HINDASGHATTA_66F07-S.L.RSTEELS | 1310401904020101 | other | 18.7588 | 17.63 | 36.3888 | 1 | 8 | 0 | 192.505 | 191.398 | 191.398 | 0 | 1.107 | 20000 | 22140 | 1 | 22140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22140 |  |  | 0 | 0 | 19485 | 0 | 19485 | 2655 | 11.9919 | 11.99 | 0.0018699 | 10-15 | 88.0081 | 88.0081 | 10026884 | 182246 | 149222 | 10059908 | 81.8794 | 27.9394 | 27.9394 | 20-30 | 81.8794 | 27.9394 | 20-30 |  | 19485 | 11.9919 | 10-15
32 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F08-KURUBARAHALLI | HINDASGHATTA_66F08-KURUBARAHALLI | 1310401904020303 | AGRI | 26.1563 | 24.576 | 50.7323 | 113 | 3 | 494 | 702.208 | 677.535 | 677.535 | 0 | 24.673 | 20000 | 493460 | 1 | 493460 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 503460 |  |  | 0 | 0 | 455631.509 | 0 | 455631.509 | 47828.491 | 9.5 | 9.5 | -4.1513e-05 | 5-10 | 90.5 | 90.5 | 15819009.36 | 2652138.89 | 2652137.127 | 15819010.36 | 99.9999 | 9.5 | 9.5 | 5-10 | 99.9999 | 9.5 | 5-10 |  | 455631.509 | 9.5 | 5-10
33 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F09-NJYSOMERAHALLI | HINDASGHATTA_66F09-NJYSOMERAHALLI | 1310401904010105 | NJY | 25.6 | 18.56 | 44.16 | 88 | 4225 | 0 | 2880.74 | 2800.05 | 2800.05 | 0 | 80.69 | 2000 | 161380 | 1 | 161380 | 0 | 0 | 0 | 0 | 90000 | 90000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251380 |  |  | 0 | 0 | 234893.15 | 0 | 234893.15 | 16486.85 | 6.5585 | 6.56 | -0.0014631 | 5-10 | 93.4415 | 93.4415 | 45571649.38 | 2733671.64 | 1475692.01 | 46829629.01 | 53.9821 | 49.5584 | 49.5584 | >30 | 53.9821 | 49.5584 | >30 |  | 234893.15 | 6.5585 | 5-10
34 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F10-HULUGULAKUNTE | HINDASGHATTA_66F10-HULUGULAKUNTE | 1310401904010106 | AGRI | 14.68 | 18.65 | 33.33 | 117 | 20 | 342 | 4074.14 | 3819.01 | 3819.01 | 0 | 255.13 | 2000 | 510260 | 1 | 510260 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520260 |  |  | 0 | 0 | 470835.896 | 0 | 470835.896 | 49424.104 | 9.4999 | 9.5 | -0.00011456 | 5-10 | 90.5001 | 90.5001 | 13162736.97 | 2741545.62 | 2741144.771 | 13163138.94 | 99.9854 | 9.5131 | 9.5131 | 5-10 | 99.9854 | 9.5131 | 5-10 |  | 470835.896 | 9.4999 | 5-10
35 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F11-NJYMAVINAMADU | HINDASGHATTA_66F11-NJYMAVINAMADU | 1310401904020304 | NJY | 22.4926 | 21.138 | 43.6306 | 56 | 2619 | 0 | 795.068 | 778.451 | 778.451 | 0 | 16.617 | 12500 | 207712.5 | 1 | 207712.5 | 0 | 0 | 0 | 0 | 12000 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219712.5 |  |  | 0 | 0 | 195455.3 | 0 | 195455.3 | 24257.2 | 11.0404 | 11.04 | 0.00042783 | 10-15 | 88.9596 | 88.9596 | 28721413.28 | 1903714.69 | 964526.69 | 29660601.28 | 50.6655 | 54.9282 | 54.9282 | >30 | 50.6655 | 54.9282 | >30 |  | 195455.3 | 11.0404 | 10-15
36 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F12-NJYYALLADAKERE | HINDASGHATTA_66F12-NJYYALLADAKERE | 1310401904020305 | NJY | 24.3494 | 22.882 | 47.2314 | 53 | 2369 | 0 | 493.568 | 484.024 | 484.024 | 0 | 9.544 | 10000 | 95440 | 1 | 95440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 5000 | 0 | 0 | 0 | 90440 |  |  | 0 | 0 | 80206.3 | 0 | 80206.3 | 10233.7 | 11.3155 | 11.32 | -0.0045422 | 10-15 | 88.6845 | 88.6845 | 18955795.66 | 1121871.15 | 532740.15 | 19544926.66 | 47.4868 | 57.8866 | 57.8866 | >30 | 47.4868 | 57.8866 | >30 |  | 80206.3 | 11.3155 | 10-15
37 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F13-CHIGALIKATTE | HINDASGHATTA_66F13-CHIGALIKATTE | 1310401904010107 | AGRI | 23.65 | 25.6 | 49.25 | 121 | 0 | 378 | 834.718 | 806.831 | 806.831 | 0 | 27.887 | 20000 | 557740 | 1 | 557740 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 567740 |  |  | 0 | 0 | 513806.09 | 0 | 513806.09 | 53933.91 | 9.4998 | 9.5 | -0.00024483 | 5-10 | 90.5002 | 90.5002 | 7652664 | 2990349.96 | 2990351.458 | 7652664 | 100.0001 | 9.4997 | 9.4997 | 5-10 | 100 | 9.4998 | 5-10 |  | 513806.09 | 9.4998 | 5-10
38 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F14-YALLADAKERE | HINDASGHATTA_66F14-YALLADAKERE | 1310401904010109 | AGRI | 25.2183 | 29.636 | 54.8543 | 116 | 0 | 230 | 1281.087 | 1253.293 | 1253.293 | 0 | 27.794 | 20000 | 555880 | 1 | 555880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82000 | 82000 | 0 | 0 | 0 | 473880 |  |  | 0 | 0 | 412300 | 0 | 412300 | 61580 | 12.9949 | 12.99 | 0.004851 | 10-15 | 87.0051 | 87.0051 | 1683690 | 2399586 | 2399586 | 1683690 | 100 | 12.9949 | 12.9949 | 10-15 | 100 | 12.9949 | 10-15 |  | 412300 | 12.9949 | 10-15
39 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F15-GOWDANAHALLY | HINDASGHATTA_66F15-GOWDANAHALLY | 1310401904010108 | AGRI | 26.2263 | 24.646 | 50.8723 | 102 | 0 | 397 | 3634.78 | 3371.97 | 3371.97 | 0 | 262.81 | 2000 | 525620 | 1 | 525620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 525620 |  |  | 0 | 0 | 475686.09 | 0 | 475686.09 | 49933.91 | 9.5 | 9.5 | 1.9025e-06 | 5-10 | 90.5 | 90.5 | 7686841 | 2768493.22 | 2768493.157 | 7686841.02 | 100 | 9.5 | 9.5 | 5-10 | 100 | 9.5 | 5-10 |  | 475686.09 | 9.5 | 5-10
40 | Non_RAPDRP | HIRIYUR | DINDAWARA | HINDASGHATTA_66 | F19-PILAJANAHALLY | HINDASGHATTA_66F19-PILAJANAHALLY | 1310401904010110 | AGRI | 26.2263 | 24.646 | 50.8723 | 102 | 0 | 250 | 783.971 | 767.778 | 767.778 | 0 | 16.193 | 20000 | 323860 | 1 | 323860 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333860 |  |  | 0 | 0 | 302143.616 | 0 | 302143.616 | 31716.384 | 9.4999 | 9.5 | -9.465e-05 | 5-10 | 90.5001 | 90.5001 | 1371213 | 1758475.22 | 1758630.682 | 1371058 | 100.0088 | 9.4919 | 9.4919 | 5-10 | 100 | 9.4999 | 5-10 |  | 302143.616 | 9.4999 | 5-10
41 | Non_RAPDRP | HIRIYUR | HARIYABBE | HIRIYUR_220 | F02-RANGENAHALLI | HIRIYUR_220F02-RANGENAHALLI | 1310401905010101 | AGRI | 20.6957 | 19.454 | 40.1497 | 113 | 1 | 407 | 707.909 | 690.496 | 690.496 | 0 | 17.413 | 20000 | 348260 | 1 | 348260 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358260 |  |  | 0 | 0 | 324225.67 | 0 | 324225.67 | 34034.33 | 9.4999 | 9.5 | -0.00010328 | 5-10 | 90.5001 | 90.5001 | 15684287 | 1888214.42 | 1886230.915 | 15686271 | 99.895 | 9.595 | 9.595 | 5-10 | 99.895 | 9.595 | 5-10 |  | 324225.67 | 9.4999 | 5-10
42 | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_220 | F03-BEERANAHALLI | HIRIYUR_220F03-BEERANAHALLI | 1310401905010102 | AGRI | 22.5526 | 21.198 | 43.7506 | 112 | 2 | 623 | 822.479 | 798.809 | 798.809 | 0 | 23.67 | 20000 | 473400 | 1 | 473400 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483400 |  |  | 0 | 0 | 437478.264 | 0 | 437478.264 | 45921.736 | 9.4997 | 9.5 | -0.00026148 | 5-10 | 90.5003 | 90.5003 | 11121984.55 | 2546247.76 | 2546248.121 | 11121984.57 | 100 | 9.4997 | 9.4997 | 5-10 | 100 | 9.4997 | 5-10 |  | 437478.264 | 9.4997 | 5-10
43 | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_220 | F04-VVPURA | HIRIYUR_220F04-VVPURA | 1310401905010103 | AGRI | 21.87 | 28.65 | 50.52 | 102 | 12 | 610 | 964.433 | 932.723 | 932.723 | 0 | 31.71 | 20000 | 634200 | 1 | 634200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 634200 |  |  | 0 | 0 | 573950.409 | 0 | 573950.409 | 60249.591 | 9.5001 | 9.5 | 9.3188e-05 | 5-10 | 90.4999 | 90.4999 | 13095051.48 | 3350346.68 | 3348972.862 | 13096424.46 | 99.959 | 9.5372 | 9.5372 | 5-10 | 99.959 | 9.5372 | 5-10 |  | 573950.409 | 9.5001 | 5-10
44 | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_220 | F05-BYDRAHALLY | HIRIYUR_220F05-BYDRAHALLY | 1310401905020301 | AGRI | 18.8788 | 23.56 | 42.4388 | 98 | 23 | 170 | 3853.27 | 3606.17 | 3606.17 | 0 | 247.1 | 2000 | 494200 | 1 | 494200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145000 | 145000 | 0 | 0 | 0 | 349200 |  |  | 0 | 0 | 303910 | 0 | 303910 | 45290 | 12.9696 | 12.97 | -0.0003551 | 10-15 | 87.0304 | 87.0304 | 3054284 | 1769005 | 1768698 | 3054591 | 99.9826 | 12.9847 | 12.9847 | 10-15 | 99.9826 | 12.9847 | 10-15 |  | 303910 | 12.9696 | 10-15
45 | Non_RAPDRP | HIRIYUR | R.N.PURA | HIRIYUR_220 | F06-HARANKATTE | HIRIYUR_220F06-HARANKATTE | 1310401905020302 | AGRI | 22.65 | 19.89 | 42.54 | 128 | 15 | 384 | 504.892 | 485.506 | 485.506 | 0 | 19.386 | 20000 | 387720 | 1 | 387720 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397720 |  |  | 0 | 0 | 359936.565 | 0 | 359936.565 | 37783.435 | 9.5 | 9.5 | 8.8002e-06 | 5-10 | 90.5 | 90.5 | 8303347.52 | 2095961.92 | 2095194.575 | 8304115.54 | 99.9634 | 9.5331 | 9.5331 | 5-10 | 99.9634 | 9.5331 | 5-10 |  | 359936.565 | 9.5 | 5-10
46 | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_220 | F08-MASKAL | HIRIYUR_220F08-MASKAL | 1310401905020303 | AGRI | 19.8988 | 22.65 | 42.5488 | 121 | 27 | 388 | 660.975 | 637.61 | 637.61 | 0 | 23.365 | 20000 | 467300 | 1 | 467300 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 477300 |  |  | 0 | 0 | 431956.996 | 0 | 431956.996 | 45343.004 | 9.4999 | 9.5 | -0.00010392 | 5-10 | 90.5001 | 90.5001 | 9607159.28 | 2515534.77 | 2514185.831 | 9608509.19 | 99.9464 | 9.5484 | 9.5484 | 5-10 | 99.9464 | 9.5484 | 5-10 |  | 431956.996 | 9.4999 | 5-10
47 | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_220 | F09-GANNAYAKANAHALLI | HIRIYUR_220F09-GANNAYAKANAHALLI | 1310401905010104 | AGRI | 24.4494 | 22.982 | 47.4314 | 119 | 3 | 202 | 105.013 | 98.163 | 98.163 | 0 | 6.85 | 20000 | 137000 | 1 | 137000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137000 |  |  | 0 | 0 | 123984.32 | 0 | 123984.32 | 13015.68 | 9.5005 | 9.5 | 0.00049635 | 5-10 | 90.4995 | 90.4995 | 219800.46 | 721755.15 | 721754.643 | 219800.46 | 99.9999 | 9.5006 | 9.5006 | 5-10 | 99.9999 | 9.5006 | 5-10 |  | 123984.32 | 9.5005 | 5-10
48 | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_220 | F10-NJYBEERANAHALLI | HIRIYUR_220F10-NJYBEERANAHALLI | 1310401905010105 | NJY | 22.6126 | 19.68 | 42.2926 | 63 | 3371 | 0 | 579.965 | 568.558 | 568.558 | 0 | 11.407 | 20000 | 228140 | 1 | 228140 | 0 | 0 | 0 | 0 | 15000 | 15000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243140 |  |  | 0 | 0 | 219248.1 | 0 | 219248.1 | 23891.9 | 9.8264 | 9.83 | -0.0036037 | 5-10 | 90.1736 | 90.1736 | 24615602.76 | 2495442.86 | 1812170.85 | 25298874.77 | 72.6192 | 34.5166 | 34.5166 | >30 | 72.6192 | 34.5166 | >30 |  | 219248.1 | 9.8264 | 5-10
49 | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_220 | F11-NJYHEMADALA | HIRIYUR_220F11-NJYHEMADALA | 1310401905020304 | NJY | 18.68 | 15.68 | 34.36 | 42 | 994 | 0 | 203.667 | 198.518 | 198.518 | 0 | 5.149 | 10000 | 51490 | 1 | 51490 | 0 | 0 | 0 | 0 | 15000 | 15000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66490 |  |  | 0 | 0 | 60433.55 | 0 | 60433.55 | 6056.45 | 9.1088 | 9.11 | -0.0011866 | 5-10 | 90.8912 | 90.8912 | 4131871.47 | 694376.54 | 506187.54 | 4320060.47 | 72.8981 | 33.742 | 33.742 | >30 | 72.8981 | 33.742 | >30 |  | 60433.55 | 9.1088 | 5-10
50 | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_220 | F12-NJYMALLENU | HIRIYUR_220F12-NJYMALLENU | 1310401905020305 | NJY | 20.6326 | 18.96 | 39.5926 | 39 | 2849 | 0 | 588.927 | 572.332 | 572.332 | 0 | 16.595 | 10000 | 165950 | 1 | 165950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 20000 | 0 | 0 | 0 | 145950 |  |  | 0 | 0 | 126698 | 0 | 126698 | 19252 | 13.1908 | 13.19 | 0.00081877 | 10-15 | 86.8092 | 86.8092 | 22658087.42 | 1397203.09 | 814651.36 | 23240639.15 | 58.3059 | 49.3852 | 49.3852 | >30 | 58.3059 | 49.3852 | >30 |  | 126698 | 13.1908 | 10-15
51 | Non_RAPDRP | HIRIYUR | R.N.PURA | HIRIYUR_220 | F13-NANDIHALLY NJY | HIRIYUR_220F13-NANDIHALLY NJY | 1310401905010107 | NJY | 7.1722 | 6.7632 | 13.9354 | 55 | 1451 | 0 | 1063.299 | 1026.837 | 1026.837 | 0 | 36.462 | 10000 | 364620 | 1 | 364620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208000 | 208000 | 0 | 0 | 0 | 156620 |  |  | 0 | 0 | 138428.85 | 0 | 138428.85 | 18191.15 | 11.6148 | 11.61 | 0.0048321 | 10-15 | 88.3852 | 88.3852 | 19450456.69 | 1670823.58 | 869208.94 | 20252071.33 | 52.0228 | 54.0196 | 54.0196 | >30 | 52.0228 | 54.0196 | >30 |  | 138428.85 | 11.6148 | 10-15
52 | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_66 | F11-CHALLAKERE WATER WORKS | HIRIYUR_66F11-CHALLAKERE WATER WORKS | 1310401902010107 | WATER WORKS | 18.9588 | 17.83 | 36.7888 | 1 | 6 | 0 | 889.208 | 867.38 | 867.38 | 0 | 21.828 | 20000 | 436560 | 1 | 436560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145000 | 145000 | 0 | 0 | 0 | 291560 |  |  | 0 | 0 | 254210 | 0 | 254210 | 37350 | 12.8104 | 12.83 | -0.019601 | 10-15 | 87.1896 | 87.1896 | 3242652.73 | 2214615.17 | 2334530.17 | 3122737.73 | 105.4147 | 8.0893 | 8.0893 | 5-10 | 100 | 12.8104 | 10-15 |  | 254210 | 12.8104 | 10-15
53 | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_66 | F03-NJYDODDAGHATTA | HIRIYUR_66F03-NJYDODDAGHATTA | 1310401902010101 | NJY | 14.59 | 14.372 | 28.962 | 56 | 1098 | 0 | 115.174 | 113.206 | 113.206 | 0 | 1.968 | 20000 | 39360 | 1 | 39360 | 0 | 0 | 0 | 0 | 20000 | 20000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59360 |  |  | 0 | 0 | 54464.53 | 0 | 54464.53 | 4895.47 | 8.2471 | 8.25 | -0.0029144 | 5-10 | 91.7529 | 91.7529 | 8592202.33 | 578305.07 | 312630.07 | 8857877.33 | 54.0597 | 50.3986 | 50.3986 | >30 | 54.0597 | 50.3986 | >30 |  | 54464.53 | 8.2471 | 5-10
54 | Non_RAPDRP | HIRIYUR | R.N.PURA | HIRIYUR_66 | F04-ADIVALA | HIRIYUR_66F04-ADIVALA | 1310401902010102 | AGRI | 15.285 | 14.382 | 29.667 | 86 | 186 | 595 | 885.749 | 856.317 | 856.317 | 0 | 29.432 | 20000 | 588640 | 1 | 588640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588640 |  |  | 0 | 0 | 532719.63 | 0 | 532719.63 | 55920.37 | 9.4999 | 9.5 | -7.305e-05 | 5-10 | 90.5001 | 90.5001 | 11690817.9 | 3120136.35 | 3135359.09 | 11675595.9 | 100.4879 | 9.0584 | 9.0584 | 5-10 | 100 | 9.4999 | 5-10 |  | 532719.63 | 9.4999 | 5-10
55 | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_66 | F07-LAKKAVANAHALLI | HIRIYUR_66F07-LAKKAVANAHALLI | 1310401902020302 | AGRI | 15.98 | 18.59 | 34.57 | 133 | 9 | 288 | 917.229 | 886.549 | 886.549 | 0 | 30.68 | 20000 | 613600 | 1 | 613600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 30000 | 0 | 0 | 0 | 583600 |  |  | 0 | 0 | 523100 | 0 | 523100 | 60500 | 10.3667 | 10.37 | -0.0033105 | 10-15 | 89.6333 | 89.6333 | 10737312 | 3044442 | 3044442 | 10737312 | 100 | 10.3667 | 10.3667 | 10-15 | 100 | 10.3667 | 10-15 |  | 523100 | 10.3667 | 10-15
bee | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_66 | F08-HABIB | HIRIYUR_66F08-HABIB | 1310401902020303 | MIXED LOAD | 11.6113 | 10.934 | 22.5453 | 42 | 501 | 0 | 1274.861 | 1259.952 | 1259.952 | 0 | 14.909 | 20000 | 298180 | 1 | 298180 | 0 | 0 | 0 | 0 | 622000 | 622000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920180 |  |  | 0 | 0 | 848098.7 | 0 | 848098.7 | 72081.3 | 7.8334 | 7.83 | 0.0033913 | 5-10 | 92.1666 | 92.1666 | 2406517.68 | 5068457.04 | 4986219.04 | 2488755.68 | 98.3775 | 9.3288 | 9.3288 | 5-10 | 98.3775 | 9.3288 | 5-10 | 0 | 848098.7 | 7.8334 | 5-10
57 | Non_RAPDRP | HIRIYUR | O&M-2 | HIRIYUR_66 | F10-HORTICULTURE COLLAGE | HIRIYUR_66F10-HORTICULTURE COLLAGE | 1310401902010106 | other | 16.0088 | 19.88 | 35.8888 | 1 | 836 | 0 | 434.262 | 431.296 | 431.296 | 0 | 2.966 | 20000 | 59320 | 1 | 59320 | 0 | 0 | 0 | 0 | 28000 | 28000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87320 | 59320 | 28000 | 0 | 0 | 79719.5 | 0 | 79719.5 | 7600.5 | 8.7042 | -184.71 | 193.4142 | 5-10 | 91.2958 | 91.2958 | 2386149.48 | 852147.84 | 570070.84 | 2668226.48 | 66.8981 | 38.9248 | 38.9248 | >30 | 66.8981 | 38.9248 | >30 |  | 79719.5 | 8.7042 | 5-10
58 | Non_RAPDRP | HIRIYUR | AIMANGALA | IMANGALA_66 | F01-GUILALU | IMANGALA_66F01-GUILALU | 1310401909010101 | AGRI | 16.89 | 17.89 | 34.78 | 114 | 0 | 8 | 218.726 | 218.726 | #N/A | #N/A | 0 | 20000 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 11865.15 | 0 | 11865.15 | -11865.15 | #DIV/0! | -1186515 | #DIV/0! | #DIV/0! |  | #DIV/0! | -9038 | 69055.18 | 69055.176 | -9038 |  |  |  | NA |  |  |  |  | 11865.15 |  | NA |  | Due to fauty AB cable feeder kept Idle
59 | Non_RAPDRP | HIRIYUR | AIMANGALA | IMANGALA_66 | F02-TAVANDI | IMANGALA_66F02-TAVANDI | 1310401909010102 | AGRI | 20.8757 | 19.634 | 40.5097 | 94 | 43 | 222 | 781.951 | 760.274 | 760.274 | 0 | 21.677 | 20000 | 433540 | 1 | 433540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433540 |  |  | 0 | 0 | 385162.94 | 0 | 385162.94 | 48377.06 | 11.1586 | 11.16 | -0.0013849 | 10-15 | 88.8414 | 88.8414 | 2007100.46 | 2251378.59 | 2241260.59 | 2017218.46 | 99.5506 | 11.5579 | 11.5579 | 10-15 | 99.5506 | 11.5579 | 10-15 |  | 385162.94 | 11.1586 | 10-15
60 | Non_RAPDRP | HIRIYUR | AIMANGALA | IMANGALA_66 | F03-BHARAMPURA | IMANGALA_66F03-BHARAMPURA | 1310401909010103 | AGRI | 20.65 | 21.65 | 42.3 | 88 | 125 | 390 | 886.304 | 852.851 | 852.851 | 0 | 33.453 | 20000 | 669060 | 1 | 669060 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 679060 |  |  | 0 | 0 | 614549.806 | 0 | 614549.806 | 64510.194 | 9.4999 | 9.5 | -7.4515e-05 | 5-10 | 90.5001 | 90.5001 | 10647756 | 3576679.92 | 3576680.945 | 10647755.05 | 100 | 9.4999 | 9.4999 | 5-10 | 100 | 9.4999 | 5-10 |  | 614549.806 | 9.4999 | 5-10
61 | Non_RAPDRP | HIRIYUR | AIMANGALA | IMANGALA_66 | F04-KALLAHATTY | IMANGALA_66F04-KALLAHATTY | 1310401909010104 | AGRI | 19.5 | 21.5 | 41 | 98 | 123 | 425 | 615.811 | 590.937 | 590.937 | 0 | 24.874 | 20000 | 497480 | 1 | 497480 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507480 |  |  | 0 | 0 | 459268.608 | 0 | 459268.608 | 48211.392 | 9.5002 | 9.5 | 0.00015607 | 5-10 | 90.4998 | 90.4998 | 14742402.41 | 2674266.99 | 2671848.524 | 14744822.41 | 99.9096 | 9.582 | 9.582 | 5-10 | 99.9096 | 9.582 | 5-10 |  | 459268.608 | 9.5002 | 5-10
62 | Non_RAPDRP | HIRIYUR | MARADIHALLY | IMANGALA_66 | F05-PALAVVANAHALLY | IMANGALA_66F05-PALAVVANAHALLY | 1310401909020301 | AGRI | 18.6 | 20.98 | 39.58 | 89 | 116 | 300 | 766.262 | 746.063 | 746.063 | 0 | 20.199 | 30000 | 605970 | 1 | 605970 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605970 |  |  | 0 | 0 | 539458 | 0 | 539458 | 66512 | 10.9761 | 10.98 | -0.0038791 | 10-15 | 89.0239 | 89.0239 | 15487983.19 | 3139818.98 | 3139818.98 | 15487983.19 | 100 | 10.9761 | 10.9761 | 10-15 | 100 | 10.9761 | 10-15 |  | 539458 | 10.9761 | 10-15
63 | Non_RAPDRP | HIRIYUR | MARADIHALLY | IMANGALA_66 | F06-BURUJINAROOPPA | IMANGALA_66F06-BURUJINAROOPPA | 1310401909020302 | AGRI | 11.6813 | 11.004 | 22.6853 | 149 | 133 | 525 | 918.355 | 884.665 | 884.665 | 0 | 33.69 | 30000 | 1010700 | 1 | 1010700 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020700 |  |  | 0 | 0 | 923732.201 | 0 | 923732.201 | 96967.799 | 9.5001 | 9.5 | 0.00012727 | 5-10 | 90.4999 | 90.4999 | 32302451 | 5376245.67 | 5376121.337 | 32302574.13 | 99.9977 | 9.5022 | 9.5022 | 5-10 | 99.9977 | 9.5022 | 5-10 |  | 923732.201 | 9.5001 | 5-10
64 | Non_RAPDRP | HIRIYUR | MARADIHALLY | IMANGALA_66 | F07-WATERWORKS | IMANGALA_66F07-WATERWORKS | 1310401909020501 | WATER WORKS | 13.5382 | 12.748 | 26.2862 | 1 | 2001 | 0 | 1061.42 | 1042.747 | 1042.747 | 0 | 18.673 | 20000 | 373460 | 1 | 373460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373460 |  |  | 0 | 0 | 333311.3 | 0 | 333311.3 | 40148.7 | 10.7505 | 10.75 | 0.00046859 | 10-15 | 89.2495 | 89.2495 | 32749918.09 | 3104625.03 | 2392838.03 | 33461705.09 | 77.0733 | 31.2124 | 31.2124 | >30 | 77.0733 | 31.2124 | >30 |  | 333311.3 | 10.7505 | 10-15
65 | Non_RAPDRP | HIRIYUR | AIMANGALA | IMANGALA_66 | F08-AIMANGALA | IMANGALA_66F08-AIMANGALA | 1310401909020502 | AGRI | 22.7826 | 21.428 | 44.2106 | 168 | 124 | 545 | 577.56 | 566.953 | 566.953 | 0 | 10.607 | 20000 | 212140 | 1 | 212140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212140 |  |  | 0 | 0 | 191987.696 | 0 | 191987.696 | 20152.304 | 9.4995 | 9.5 | -0.0004695 | 5-10 | 90.5005 | 90.5005 | 4196673.88 | 1117778.5 | 1117777.224 | 4196674.91 | 99.9999 | 9.4996 | 9.4996 | 5-10 | 99.9999 | 9.4996 | 5-10 |  | 191987.696 | 9.4995 | 5-10
66 | Non_RAPDRP | HIRIYUR | AIMANGALA | IMANGALA_66 | F09-NJYMETIKURKE | IMANGALA_66F09-NJYMETIKURKE | 1310401909010105 | AGRI | 19.0988 | 17.97 | 37.0688 | 69 | 568 | 156 | 544.56 | 521.931 | 521.931 | 0 | 22.629 | 20000 | 452580 | 1 | 452580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135000 | 135000 | 0 | 0 | 0 | 317580 |  |  | 0 | 0 | 275031 | 0 | 275031 | 42549 | 13.3979 | 13.4 | -0.002116 | 10-15 | 86.6021 | 86.6021 | 5879610.94 | 1613384.5 | 1605234.5 | 5887760.94 | 99.4949 | 13.8354 | 13.8354 | 10-15 | 99.4949 | 13.8354 | 10-15 |  | 275031 | 13.3979 | 10-15
67 | Non_RAPDRP | HIRIYUR | AIMANGALA | IMANGALA_66 | F10-MALLARASANAHATTI | IMANGALA_66F10-MALLARASANAHATTI | 1310401909010106 | AGRI | 11.7213 | 11.044 | 22.7653 | 123 | 1 | 294 | 752.144 | 732.875 | 732.875 | 0 | 19.269 | 20000 | 385380 | 1 | 385380 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395380 |  |  | 0 | 0 | 357819.247 | 0 | 357819.247 | 37560.753 | 9.4999 | 9.5 | -8.7764e-05 | 5-10 | 90.5001 | 90.5001 | 6864361 | 2082507.86 | 2082507.826 | 6864360.99 | 100 | 9.4999 | 9.4999 | 5-10 | 100 | 9.4999 | 5-10 |  | 357819.247 | 9.4999 | 5-10
68 | Non_RAPDRP | HIRIYUR | MARADIHALLY | IMANGALA_66 | F11-ECL | IMANGALA_66F11-ECL | 1310401909010107 | INDUSTRIAL | 22.8126 | 21.458 | 44.2706 | 1 | 8 | 0 | 198.223 | 197.798 | 197.798 | 0 | 0.425 | 20000 | 8500 | 1 | 8500 | 0 | 0 | 0 | 0 | 6500 | 6500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 |  |  | 0 | 0 | 13726 | 0 | 13726 | 1274 | 8.4933 | 8.49 | 0.0033333 | 5-10 |  | 91.5067 | -39407 | 188427 | 200746 | -51726 | 106.5378 | 100 | 2.5108 | >30 | 100 | 8.4933 | 5-10 |  | 13726 | 8.4933 | 5-10
69 | Non_RAPDRP | HIRIYUR | MARADIHALLY | IMANGALA_66 | F12-MARADIHALLI | IMANGALA_66F12-MARADIHALLI | 1310401909020503 | AGRI | 19.1288 | 18.2 | 37.3288 | 118 | 11 | 288 | 656.106 | 636.288 | 636.288 | 0 | 19.818 | 20000 | 396360 | 1 | 396360 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406360 |  |  | 0 | 0 | 367756.407 | 0 | 367756.407 | 38603.593 | 9.4999 | 9.5 | -0.00014937 | 5-10 | 90.5001 | 90.5001 | 5479925 | 2140341.73 | 2140342.188 | 5479925 | 100 | 9.4998 | 9.4998 | 5-10 | 100 | 9.4999 | 5-10 |  | 367756.407 | 9.4999 | 5-10
70 | Non_RAPDRP | HIRIYUR | MARADIHALLY | IMANGALA_66 | F13-NONABI | IMANGALA_66F13-NONABI | 1310401909020504 | AGRI | 15.445 | 14.542 | 29.987 | 109 | 19 | 403 | 605.675 | 587.626 | 587.626 | 0 | 18.049 | 20000 | 360980 | 1 | 360980 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370980 |  |  | 0 | 0 | 335735.712 | 0 | 335735.712 | 35244.288 | 9.5003 | 9.5 | 0.00032023 | 5-10 | 90.4997 | 90.4997 | 11523484.55 | 1954112.17 | 1954109.108 | 11523487.55 | 99.9998 | 9.5005 | 9.5005 | 5-10 | 99.9998 | 9.5005 | 5-10 |  | 335735.712 | 9.5003 | 5-10
71 | Non_RAPDRP | HIRIYUR | MARADIHALLY | IMANGALA_66 | F14-NJYMDKOTE | IMANGALA_66F14-NJYMDKOTE | 1310401909020505 | NJY | 17.3019 | 16.286 | 33.5879 | 63 | 4678 | 0 | 861.526 | 845.249 | 845.249 | 0 | 16.277 | 20000 | 325540 | 1 | 325540 | 0 | 0 | 0 | 0 | 25000 | 25000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350540 |  |  | 0 | 0 | 318636.75 | 0 | 318636.75 | 31903.25 | 9.1012 | 9.1 | 0.0011725 | 5-10 | 90.8988 | 90.8988 | 45054794.72 | 3215827.71 | 2154312.91 | 46116309.52 | 66.9909 | 39.106 | 39.106 | >30 | 66.9909 | 39.106 | >30 |  | 318636.75 | 9.1012 | 5-10
72 | Non_RAPDRP | HIRIYUR | MARADIHALLY | IMANGALA_66 | F15-C.S.HALLY NJY | IMANGALA_66F15-C.S.HALLY NJY | 1310401909030501 | NJY | 18.4255 | 17.3415 | 35.767 | 56 | 0 | 0 | 101.939 | 101.939 | #N/A | #N/A | 0 | 20000 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #N/A | #DIV/0! | #DIV/0! |  | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 0 |  | NA |  | Due to fauty AB cable feeder kept Idle
73 | Non_RAPDRP | HIRIYUR | AIMANGALA | IMANGALA_66 | F19-NJY KC ROPPA | IMANGALA_66F19-NJY KC ROPPA | 1310401909020506 | NJY | 20.7115 | 19.4884 | 40.1999 | 61 | 1763 | 0 | 448.361 | 439.019 | 439.019 | 0 | 9.342 | 20000 | 186840 | 1 | 186840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 45000 | 0 | 0 | 0 | 141840 |  |  | 0 | 0 | 127442.1 | 0 | 127442.1 | 14397.9 | 10.1508 | 10.15 | 0.00080372 | 10-15 | 89.8492 | 89.8492 | 19477014.19 | 1326707.95 | 784821.95 | 20018900.19 | 59.1556 | 46.8492 | 46.8492 | >30 | 59.1556 | 46.8492 | >30 |  | 127442.1 | 10.1508 | 10-15
74 | Non_RAPDRP | HIRIYUR | AIMANGALA | IMANGALA_66 | F20-KOVERAHATTI | IMANGALA_66F20-KOVERAHATTI | 1310401909010109 | AGRI | 17.3319 | 16.316 | 33.6479 | 118 | 0 | 370 | 656.806 | 637.11 | 637.11 | 0 | 19.696 | 20000 | 393920 | 1 | 393920 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403920 |  |  | 0 | 0 | 365546.52 | 0 | 365546.52 | 38373.48 | 9.5003 | 9.5 | 0.00026738 | 5-10 | 90.4997 | 90.4997 | 24103167 | 2127480.19 | 2127480.681 | 24103166.94 | 100 | 9.5002 | 9.5002 | 5-10 | 100 | 9.5003 | 5-10 |  | 365546.52 | 9.5003 | 5-10
75 | Non_RAPDRP | HIRIYUR | R.N.PURA | JAVAGONDANAHALLI_66 | F01-GORALADUKU | JAVAGONDANAHALLI_66F01-GORALADUKU | 1310401903010101 | AGRI | 15.495 | 14.592 | 30.087 | 121 | 0 | 107 | 458.06 | 300.33 | 300.33 | 0 | 157.73 | 2000 | 315460 | 1 | 315460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130000 | 130000 | 0 | 0 | 0 | 185460 |  |  | 0 | 0 | 161400 | 0 | 161400 | 24060 | 12.9731 | 12.97 | 0.0031478 | 10-15 | 87.0269 | 87.0269 | 3058794 | 939348 | 939348 | 3058794 | 100 | 12.9731 | 12.9731 | 10-15 | 100 | 12.9731 | 10-15 |  | 161400 | 12.9731 | 10-15
76 | Non_RAPDRP | HIRIYUR | R.N.PURA | JAVAGONDANAHALLI_66 | F02-NJYANESIDRI | JAVAGONDANAHALLI_66F02-NJYANESIDRI | 1310401903010102 | NJY | 19.1988 | 18.07 | 37.2688 | 65 | 3342 | 0 | 643.47 | 527.87 | 527.87 | 0 | 115.6 | 2000 | 231200 | 1 | 231200 | 0 | 0 | 0 | 0 | 12000 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243200 |  |  | 0 | 0 | 218342.628 | 0 | 218342.628 | 24857.372 | 10.221 | 10.22 | 0.00095888 | 10-15 | 89.779 | 89.779 | 19706084.14 | 2274694.07 | 1712059.171 | 20268719.02 | 75.2655 | 32.4274 | 32.4274 | >30 | 75.2655 | 32.4274 | >30 |  | 218342.628 | 10.221 | 10-15
77 | Non_RAPDRP | HIRIYUR | R.N.PURA | JAVAGONDANAHALLI_66 | F03-JAVAGONDANAHALLI | JAVAGONDANAHALLI_66F03-JAVAGONDANAHALLI | 1310401903020301 | AGRI | 21.5 | 23.65 | 45.15 | 116 | 59 | 323 | 2516.94 | 2229.31 | 2229.31 | 0 | 287.63 | 2000 | 575260 | 1 | 575260 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585260 |  |  | 0 | 0 | 529658.896 | 0 | 529658.896 | 55601.104 | 9.5002 | 9.5 | 0.00023989 | 5-10 |  | 90.4998 | 9398297 | 3082616.22 | 3082614.928 | 9398297 | 100 | 100 | 9.5003 | >30 |  |  |  |  | 529658.896 |  | NA
78 | Non_RAPDRP | HIRIYUR | R.N.PURA | JAVAGONDANAHALLI_66 | F04-KTNHALLI | JAVAGONDANAHALLI_66F04-KTNHALLI | 1310401903010104 | AGRI | 21.0657 | 19.824 | 40.8897 | 174 | 1 | 357 | 1282.81 | 1254.715 | 1254.715 | 0 | 28.095 | 20000 | 561900 | 1 | 561900 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571900 |  |  | 0 | 0 | 517570.967 | 0 | 517570.967 | 54329.033 | 9.4997 | 9.5 | -0.00025651 | 5-10 | 90.5003 | 90.5003 | 12532254 | 3012262.07 | 3012263.149 | 12532254 | 100 | 9.4997 | 9.4997 | 5-10 | 100 | 9.4997 | 5-10 |  | 517570.967 | 9.4997 | 5-10
79 | Non_RAPDRP | HIRIYUR | R.N.PURA | JAVAGONDANAHALLI_66 | F06-OBALAPUR | JAVAGONDANAHALLI_66F06-OBALAPUR | 1310401903010103 | AGRI | 19.2288 | 18.1 | 37.3288 | 131 | 0 | 455 | 60.051 | 26.765 | 26.765 | 0 | 33.286 | 20000 | 665720 | 1 | 665720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438420 | 665720 | -227300 | 0 | 0 | 602478.156 | 0 | 602478.156 | -164058.156 | -37.4203 | 9.5 | -46.9203 | <0 | 90.4694 | 90.4694 | 9868221 | 3506422.96 | 3506422.749 | 9868220.98 | 100 | 9.5306 | 9.5306 | 5-10 | 100 | 9.5306 | 5-10 |  | 602478.156 | 9.5306 | 5-10
80 | Non_RAPDRP | HIRIYUR | R.N.PURA | JAVAGONDANAHALLI_66 | F07-NJYPILALI | JAVAGONDANAHALLI_66F07-NJYPILALI | 1310401903020302 | NJY | 15.545 | 14.642 | 30.187 | 95 | 1500 | 0 | 1051.7 | 975.98 | 975.98 | 0 | 75.72 | 2000 | 151440 | 1 | 151440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76000 | 76000 | 0 | 0 | 0 | 75440 |  |  | 0 | 0 | 67916 | 0 | 67916 | 7524 | 9.9735 | 9.97 | 0.0034889 | 5-10 | 90.0265 | 90.0265 | 19641145.07 | 775247.85 | 283004.85 | 20133388.07 | 36.5051 | 67.1357 | 67.1357 | >30 | 36.5051 | 67.1357 | >30 |  | 67916 | 9.9735 | 5-10
81 | Non_RAPDRP | HIRIYUR | R.N.PURA | JAVAGONDANAHALLI_66 | F08-GOLDENEEDS | JAVAGONDANAHALLI_66F08-GOLDENEEDS | 1310401903020303 | INDUSTRIAL | 19.2488 | 18.12 | 37.3688 | 3 | 9 | 0 | 2488.676 | 2415.601 | 2415.601 | 0 | 73.075 | 10000 | 730750 | 1 | 730750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730750 |  |  | 0 | 0 | 663940 | 0 | 663940 | 66810 | 9.1427 | 9.14 | 0.0026616 | 5-10 | 90.8573 | 90.8573 | 1806277 | 6000110 | 6364868 | 1441519 | 106.0792 | 3.6193 | 3.6193 | 0-5 | 100 | 9.1427 | 5-10 |  | 663940 | 9.1427 | 5-10
82 | Non_RAPDRP | HIRIYUR | R.N.PURA | JAVAGONDANAHALLI_66 | F09-RANGNATHPURA | JAVAGONDANAHALLI_66F09-RANGNATHPURA | 1310401903010105 | AGRI | 21.1057 | 19.864 | 40.9697 | 128 | 78 | 284 | 898.018 | 867.69 | 867.69 | 0 | 30.328 | 20000 | 606560 | 1 | 606560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 45000 | 0 | 0 | 0 | 561560 |  |  | 0 | 0 | 494661 | 0 | 494661 | 66899 | 11.9131 | 11.91 | 0.0030636 | 10-15 | 88.0869 | 88.0869 | 16983517.24 | 2879343.21 | 2879343.21 | 16983517.24 | 100 | 11.9131 | 11.9131 | 10-15 | 100 | 11.9131 | 10-15 |  | 494661 | 11.9131 | 10-15
83 | Non_RAPDRP | HIRIYUR | R.N.PURA | JAVAGONDANAHALLI_66 | F10-SURAPPANAHATTY | JAVAGONDANAHALLI_66F10-SURAPPANAHATTY | 1310401903020304 | AGRI | 12.3093 | 13.56 | 25.8693 | 131 | 0 | 289 | 66.663 | 33.086 | #N/A | #N/A | 33.577 | 20000 | 671540 | 1 | 671540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 70000 | 0 | 0 | 0 | 601540 |  |  | 0 | 0 | 518600 | 0 | 518600 | 82940 | 13.7879 | 13.79 | -0.0020557 | 10-15 | 86.2121 | 86.2121 | 5523207 | 3018252 | 3018252 | 5523207 | 100 | 13.7879 | 13.7879 | 10-15 | 100 | 13.7879 | 10-15 |  | 518600 | 13.7879 | 10-15
84 | Non_RAPDRP | HIRIYUR | R.N.PURA | JAVAGONDANAHALLI_66 | F05-KRISHNAGIRI | JAVAGONDANAHALLI_66F05-KRISHNAGIRI | 1310401903010108 | AGRI | 16.89 | 18.65 | 35.54 | 109 | 0 | 224 | 381.399 | 355.158 | 355.158 | 0 | 26.241 | 20000 | 524820 | 1 | 524820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 75000 | 0 | 0 | 0 | 449820 |  |  | 0 | 0 | 397300 | 0 | 397300 | 52520 | 11.6758 | 11.68 | -0.0042186 | 10-15 | 88.3242 | 88.3242 | 11667182 | 2312286 | 2312286 | 11667182 | 100 | 11.6758 | 11.6758 | 10-15 | 100 | 11.6758 | 10-15 |  | 397300 | 11.6758 | 10-15
85 | Non_RAPDRP | HIRIYUR | R.N.PURA | JAVAGONDANAHALLI_66 | F13-KARIYALA | JAVAGONDANAHALLI_66F13-KARIYALA | 1310401903010107 | AGRI | 17.65 | 19.6 | 37.25 | 98 | 147 | 326 | 2902.65 | 2658.65 | 2658.65 | 0 | 244 | 2000 | 488000 | 1 | 488000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 488000 |  |  | 0 | 0 | 441641.315 | 0 | 441641.315 | 46358.685 | 9.4997 | 9.5 | -0.00026947 | 5-10 | 90.5003 | 90.5003 | 7174031 | 2571691.26 | 2572770.342 | 7172953 | 100.042 | 9.4618 | 9.4618 | 5-10 | 100 | 9.4997 | 5-10 |  | 441641.315 | 9.4997 | 5-10
86 | Non_RAPDRP | HIRIYUR | HARIYABBE | KALAMARANAHALLI_66 | F02-BURUDUKUNTE | KALAMARANAHALLI_66F02-BURUDUKUNTE | 1310401903020900 | AGRI | 12.62 | 13.65 | 26.27 | 92 | 50 | 225 | 696.964 | 670.157 | 670.157 | 0 | 26.807 | 20000 | 536140 | 1 | 536140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 50000 | 0 | 0 | 0 | 486140 | 486140 | 0 | 0 | 0 | 438100 | 0 | 438100 | 48040 | 9.8819 | 18.29 | -8.4081 | 5-10 | 90.1181 | 90.1181 | 9804610 | 2549742 | 2549742 | 9804610 | 100 | 9.8819 | 9.8819 | 5-10 | 100 | 9.8819 | 5-10 |  | 438100 | 9.8819 | 5-10
87 | Non_RAPDRP | HIRIYUR | HARIYABBE | KALAMARANAHALLI_66 | F11-PUMP HOUSE (MI&GWD) | KALAMARANAHALLI_66F11-PUMP HOUSE (MI&GWD) | 1310402904020303 | WATER WORKS | 2.1 | 0 | 2.1 | 1 | 2 | 0 | 878.8 | 875.81 | 875.81 | 0 | 2.99 | 2000 | 5980 | 1 | 5980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5980 |  |  | 0 | 0 | 5887.5 | 0 | 5887.5 | 92.5 | 1.5468 | 1.55 | -0.0031773 | 0-5 | 98.4532 | 98.4532 | 13252084 | 934522 | 0 | 14186606 | 0 | 100 | 100 | >30 | 0 | 100 | >30 | 0 | 5887.5 | 1.5468 | 0-5
88 | Non_RAPDRP | HIRIYUR | MARADIHALLY | SANIKERE | F05-SONDEKERE | SANIKEREF05-SONDEKERE | 1310401903090900 | AGRI | 13.6 | 14.8 | 28.4 | 102 | 0 | 216 | 689.626 | 665.541 | #N/A | #N/A | 24.085 | 20000 | 481700 | 1 | 481700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 60000 | 0 | 0 | 0 | 421700 | 421700 | 0 | 0 | 0 | 379600 | 0 | 379600 | 42100 | 9.9834 | 21.2 | -11.2166 | 5-10 | 90.0166 | 90.0166 | 8806017 | 2209272 | 2209272 | 8806017 | 100 | 9.9834 | 9.9834 | 5-10 | 100 | 9.9834 | 5-10 |  | 379600 | 9.9834 | 5-10
89 | Non_RAPDRP | HIRIYUR | HARIYABBE | PD KOTE_66 | F09-MADDIHALLY | PD KOTE_66F09-MADDIHALLY | 1310401908010101 | AGRI | 13.1593 | 16.8 | 29.9593 | 106 | 3 | 385 | 8662.5 | 8333 | 8333 | 0 | 329.5 | 2000 | 659000 | 1 | 659000 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 669000 |  |  | 0 | 0 | 605444.373 | 0 | 605444.373 | 63555.627 | 9.5001 | 9.5 | 9.3722e-05 | 5-10 | 90.4999 | 90.4999 | 15070710 | 3523685.72 | 3523686.143 | 15070710 | 100 | 9.5001 | 9.5001 | 5-10 | 100 | 9.5001 | 5-10 |  | 605444.373 | 9.5001 | 5-10
90 | Non_RAPDRP | HIRIYUR | HARIYABBE | PD KOTE_66 | F02-PD-KOTE | PD KOTE_66F02-PD-KOTE | 1310401908010102 | AGRI | 18.68 | 19.6 | 38.28 | 112 | 4 | 307 | 881.336 | 853.97 | 853.97 | 0 | 27.366 | 20000 | 547320 | 1 | 547320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547320 |  |  | 0 | 0 | 495324.778 | 0 | 495324.778 | 51995.222 | 9.5 | 9.5 | -3.2522e-05 | 5-10 | 90.5 | 90.5 | 10298574 | 2882790.63 | 2882790.109 | 10298574 | 100 | 9.5 | 9.5 | 5-10 | 100 | 9.5 | 5-10 |  | 495324.778 | 9.5 | 5-10
91 | Non_RAPDRP | HIRIYUR | HARIYABBE | PD KOTE_66 | F05-HALAGALADDI NJY | PD KOTE_66F05-HALAGALADDI NJY | 1310401908010105 | NJY | 13.1793 | 14.43 | 27.6093 | 58 | 2264 | 0 | 13116.6 | 12902.3 | 12902.3 | 0 | 214.3 | 1000 | 214300 | 1 | 214300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116000 | 116000 | 0 | 0 | 0 | 98300 |  |  | 0 | 0 | 87018.7 | 0 | 87018.7 | 11281.3 | 11.4764 | 11.48 | -0.0036012 | 10-15 | 88.5236 | 88.5236 | 28966922.27 | 1105777.86 | 746613.86 | 29326086.27 | 67.5193 | 40.2295 | 40.2295 | >30 | 67.5193 | 40.2295 | >30 |  | 87018.7 | 11.4764 | 10-15
92 | Non_RAPDRP | HIRIYUR | R.N.PURA | RANGANATHAPURA_66 | F01-KUNDALAGURA | RANGANATHAPURA_66F01-KUNDALAGURA | 1310401901010101 | AGRI | 16.8 | 18.6 | 35.4 | 116 | 18 | 506 | 80.664 | 52.369 | 52.369 | 0 | 28.295 | 20000 | 565900 | 1 | 565900 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575900 |  |  | 0 | 0 | 521190.988 | 0 | 521190.988 | 54709.012 | 9.4997 | 9.5 | -0.00025838 | 5-10 | 90.5003 | 90.5003 | 20112130 | 3033330.4 | 3033331.384 | 20112130 | 100 | 9.4997 | 9.4997 | 5-10 | 100 | 9.4997 | 5-10 |  | 521190.988 | 9.4997 | 5-10
93 | Non_RAPDRP | HIRIYUR | R.N.PURA | RANGANATHAPURA_66 | F02-KODIHALLI | RANGANATHAPURA_66F02-KODIHALLI | 1310401901010102 | AGRI | 15.8 | 16.8 | 32.6 | 121 | 6 | 629 | 1104.09 | 1061.959 | 1061.959 | 0 | 42.131 | 20000 | 842620 | 1 | 842620 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 852620 |  |  | 0 | 0 | 771618.891 | 0 | 771618.891 | 81001.109 | 9.5003 | 9.5 | 0.00025908 | 5-10 | 90.4997 | 90.4997 | 20251926 | 4490821.78 | 4490821.551 | 20251926 | 100 | 9.5003 | 9.5003 | 5-10 | 100 | 9.5003 | 5-10 |  | 771618.891 | 9.5003 | 5-10
94 | Non_RAPDRP | HIRIYUR | R.N.PURA | RANGANATHAPURA_66 | F03-UPPALAGERE | RANGANATHAPURA_66F03-UPPALAGERE | 1310401901010103 | AGRI | 14.6 | 18.5 | 33.1 | 109 | 3 | 626 | 637.654 | 614.582 | 614.582 | 0 | 23.072 | 20000 | 461440 | 1 | 461440 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471440 |  |  | 0 | 0 | 426653.941 | 0 | 426653.941 | 44786.059 | 9.4998 | 9.5 | -0.00015718 | 5-10 | 90.5002 | 90.5002 | 28902752 | 2483128.08 | 2483125.884 | 28902752.85 | 99.9999 | 9.4999 | 9.4999 | 5-10 | 99.9999 | 9.4999 | 5-10 |  | 426653.941 | 9.4998 | 5-10
95 | Non_RAPDRP | HIRIYUR | R.N.PURA | RANGANATHAPURA_66 | F04-SHIVAPURA | RANGANATHAPURA_66F04-SHIVAPURA | 1310401901010104 | AGRI | 18.9 | 20.6 | 39.5 | 99 | 2 | 330 | 830.195 | 808.305 | 808.305 | 0 | 21.89 | 20000 | 437800 | 1 | 437800 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 447800 |  |  | 0 | 0 | 405259.563 | 0 | 405259.563 | 42540.437 | 9.4999 | 9.5 | -0.00012573 | 5-10 | 90.5001 | 90.5001 | 10373365 | 2358609.27 | 2358610.755 | 10373363.85 | 100.0001 | 9.4998 | 9.4998 | 5-10 | 100 | 9.4999 | 5-10 |  | 405259.563 | 9.4999 | 5-10
96 | Non_RAPDRP | HIRIYUR | R.N.PURA | RANGANATHAPURA_66 | F05-PITTLALI | RANGANATHAPURA_66F05-PITTLALI | 1310401901020301 | AGRI | 16.9 | 18.3 | 35.2 | 115 | 98 | 420 | 780.43 | 767.469 | 767.469 | 0 | 12.961 | 20000 | 259220 | 1 | 259220 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269220 |  |  | 0 | 0 | 243645.416 | 0 | 243645.416 | 25574.584 | 9.4995 | 9.5 | -0.00048882 | 5-10 | 90.5005 | 90.5005 | 23015245 | 1418016.23 | 1418016.372 | 23015245 | 100 | 9.4995 | 9.4995 | 5-10 | 100 | 9.4995 | 5-10 |  | 243645.416 | 9.4995 | 5-10
97 | Non_RAPDRP | HIRIYUR | R.N.PURA | RANGANATHAPURA_66 | F06-ALURU | RANGANATHAPURA_66F06-ALURU | 1310401901020302 | AGRI | 16.5 | 18.3 | 34.8 | 125 | 51 | 331 | 760.069 | 735.23 | 735.23 | 0 | 24.839 | 20000 | 496780 | 1 | 496780 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506780 |  |  | 0 | 0 | 458637.061 | 0 | 458637.061 | 48142.939 | 9.4998 | 9.5 | -0.00022909 | 5-10 | 90.5002 | 90.5002 | 13157180.72 | 2678754.92 | 2665857.791 | 13170077.73 | 99.5185 | 9.9355 | 9.9355 | 5-10 | 99.5185 | 9.9355 | 5-10 |  | 458637.061 | 9.4998 | 5-10
98 | Non_RAPDRP | HIRIYUR | R.N.PURA | RANGANATHAPURA_66 | F07-NJYARANAKATTE | RANGANATHAPURA_66F07-NJYARANAKATTE | 1310401901020303 | NJY | 22.65 | 18.96 | 41.61 | 62 | 3427 | 0 | 820.345 | 808.603 | 808.603 | 0 | 11.742 | 20000 | 234840 | 1 | 234840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 12000 | 0 | 0 | 0 | 222840 |  |  | 0 | 0 | 200712.75 | 0 | 200712.75 | 22127.25 | 9.9297 | 9.93 | -0.00034195 | 5-10 | 90.0703 | 90.0703 | 31476517.33 | 2081334.28 | 1274269.14 | 32283582.47 | 61.2237 | 44.8556 | 44.8556 | >30 | 61.2237 | 44.8556 | >30 | 0 | 200712.75 | 9.9297 | 5-10
99 | Non_RAPDRP | HIRIYUR | R.N.PURA | RANGANATHAPURA_66 | F09-IKKANURU | RANGANATHAPURA_66F09-IKKANURU | 1310401901020304 | AGRI | 16.58 | 18.9 | 35.48 | 119 | 0 | 290 | 5107.97 | 4811.4 | 4811.4 | 0 | 296.57 | 2000 | 593140 | 1 | 593140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 593140 |  |  | 0 | 0 | 513100 | 0 | 513100 | 80040 | 13.4943 | 13.49 | 0.0042847 | 10-15 | 86.5057 | 86.5057 | 13097257 | 2986242 | 2986242 | 13097257 | 100 | 13.4943 | 13.4943 | 10-15 | 100 | 13.4943 | 10-15 |  | 513100 | 13.4943 | 10-15
100 | Non_RAPDRP | HIRIYUR | R.N.PURA | RANGANATHAPURA_66 | F10-HOSAYALNADU | RANGANATHAPURA_66F10-HOSAYALNADU | 1310401901010301 | AGRI | 14.6 | 18.65 | 33.25 | 121 | 0 | 212 | 693.09 | 604.52 | 604.52 | 0 | 88.57 | 2000 | 177140 | 1 | 177140 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187140 |  |  | 0 | 0 | 169361.474 | 0 | 169361.474 | 17778.526 | 9.5001 | 9.5 | 0.00012077 | 5-10 | 90.4999 | 90.4999 | 11842510 | 985683.87 | 985683.669 | 11842510.2 | 100 | 9.5001 | 9.5001 | 5-10 | 100 | 9.5001 | 5-10 |  | 169361.474 | 9.5001 | 5-10
101 | Non_RAPDRP | HIRIYUR | R.N.PURA | RANGANATHAPURA_66 | F08-NJY LAKSHMIPURA | RANGANATHAPURA_66F08-NJY LAKSHMIPURA | 1310401901010105 | NJY | 19.4288 | 18.3 | 37.7288 | 48 | 4071 | 0 | 756.81 | 740.67 | 740.67 | 0 | 16.14 | 20000 | 322800 | 1 | 322800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 15000 | 0 | 0 | 0 | 307800 |  |  | 0 | 0 | 266840.677 | 0 | 266840.677 | 40959.323 | 13.3071 | 13.31 | -0.0028775 | 10-15 | 86.6929 | 86.6929 | 50721362.9 | 2665891.34 | 886649.33 | 52500604.9 | 33.259 | 71.1668 | 71.1668 | >30 | 33.259 | 71.1668 | >30 | 0 | 266840.677 | 13.3071 | 10-15
102 | Non_RAPDRP | HIRIYUR | HARIYABBE | RANGENAHALLI_66 | F08-T OBENAHALLY | RANGENAHALLI_66F08-T OBENAHALLY | 1310401907010101 | AGRI | 15.745 | 14.842 | 30.587 | 117 | 0 | 414 | 9976.1 | 9818.2 | 9818.2 | 0 | 157.9 | 2000 | 315800 | 1 | 315800 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325800 |  |  | 0 | 0 | 294849.625 | 0 | 294849.625 | 30950.375 | 9.4998 | 9.5 | -0.00019184 | 5-10 | 90.5002 | 90.5002 | 28424084 | 1716023.39 | 1716024.838 | 28424084.05 | 100.0001 | 9.4997 | 9.4997 | 5-10 | 100 | 9.4998 | 5-10 |  | 294849.625 | 9.4998 | 5-10
103 | Non_RAPDRP | HIRIYUR | HARIYABBE | RANGENAHALLI_66 | F02-SHIVAGANGA | RANGENAHALLI_66F02-SHIVAGANGA | 1310401907010102 | AGRI | 19.4488 | 18.32 | 37.7688 | 101 | 99 | 310 | 208.47 | 199.226 | 199.226 | 0 | 9.244 | 20000 | 184880 | 1 | 184880 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194880 |  |  | 0 | 0 | 176367.736 | 0 | 176367.736 | 18512.264 | 9.4993 | 9.5 | -0.00068555 | 5-10 | 90.5007 | 90.5007 | 9427851.03 | 1028186.74 | 1026200.173 | 9429838.03 | 99.8068 | 9.6742 | 9.6742 | 5-10 | 99.8068 | 9.6742 | 5-10 |  | 176367.736 | 9.4993 | 5-10
104 | Non_RAPDRP | HIRIYUR | HARIYABBE | RANGENAHALLI_66 | F03-AMBALAGERE | RANGENAHALLI_66F03-AMBALAGERE | 1310401907010103 | AGRI | 21.0015 | 19.7784 | 40.7799 | 112 | 10 | 445 | 428.236 | 403.519 | 403.519 | 0 | 24.717 | 20000 | 494340 | 1 | 494340 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 504340 |  |  | 0 | 0 | 456428.81 | 0 | 456428.81 | 47911.19 | 9.4998 | 9.5 | -0.00022009 | 5-10 | 90.5002 | 90.5002 | 15189244.32 | 2657145.26 | 2656394.64 | 15189995.26 | 99.9718 | 9.5253 | 9.5253 | 5-10 | 99.9718 | 9.5253 | 5-10 |  | 456428.81 | 9.4998 | 5-10
105 | Non_RAPDRP | HIRIYUR | HARIYABBE | RANGENAHALLI_66 | F04-BAGAVATI | RANGENAHALLI_66F04-BAGAVATI | 1310401907010104 | AGRI | 23.1626 | 21.808 | 44.9706 | 106 | 7 | 429 | 445.433 | 425.65 | 425.65 | 0 | 19.783 | 20000 | 395660 | 1 | 395660 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405660 |  |  | 0 | 0 | 367123.007 | 0 | 367123.007 | 38536.993 | 9.4998 | 9.5 | -0.00017428 | 5-10 | 90.5002 | 90.5002 | 8557355 | 2190757.98 | 2046614.583 | 8701498.01 | 93.4204 | 15.4544 | 15.4544 | 15-20 | 93.4204 | 15.4544 | 15-20 |  | 367123.007 | 9.4998 | 5-10
106 | Non_RAPDRP | HIRIYUR | HARIYABBE | RANGENAHALLI_66 | F05-NJY RANGENAHALLY | RANGENAHALLI_66F05-NJY RANGENAHALLY | 1310401907010106 | NJY | 22.3306 | 21.0275 | 43.3581 | 42 | 1405 | 0 | 348.818 | 338.979 | 338.979 | 0 | 9.839 | 10000 | 98390 | 1 | 98390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 45000 | 0 | 0 | 0 | 53390 |  |  | 0 | 0 | 46178 | 0 | 46178 | 7212 | 13.5081 | 13.51 | -0.0018524 | 10-15 | 86.4919 | 86.4919 | 18601008.76 | 615702.95 | 362363.95 | 18854347.76 | 58.8537 | 49.0963 | 49.0963 | >30 | 58.8537 | 49.0963 | >30 |  | 46178 | 13.5081 | 10-15
107 | Non_RAPDRP | HIRIYUR | HARIYABBE | RANGENAHALLI_66 | F06-SIDDESHWARA | RANGENAHALLI_66F06-SIDDESHWARA | 1310401907020301 | AGRI | 16.8892 | 20.38 | 37.2692 | 129 | 3 | 239 | 11029.3 | 10780.7 | #N/A | #N/A | 248.6 | 2000 | 497200 | 1 | 497200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 15000 | 0 | 0 | 0 | 482200 |  |  | 0 | 0 | 425600 | 0 | 425600 | 56600 | 11.7379 | 11.74 | -0.0021319 | 10-15 | 88.2621 | 88.2621 | 11416025 | 2476992 | 2476992 | 11416025 | 100 | 11.7379 | 11.7379 | 10-15 | 100 | 11.7379 | 10-15 |  | 425600 | 11.7379 | 10-15
108 | Non_RAPDRP | HIRIYUR | HARIYABBE | RANGENAHALLI_66 | F07-NJYAINAHALLY | RANGENAHALLI_66F07-NJYAINAHALLY | 1310401907010105 | NJY | 15.69 | 13.6 | 29.29 | 42 | 2531 | 0 | 7355.2 | 7245.6 | 7245.6 | 0 | 109.6 | 1000 | 109600 | 1 | 109600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 30000 | 0 | 0 | 0 | 79600 |  |  | 0 | 0 | 69901 | 0 | 69901 | 9699 | 12.1847 | 12.18 | 0.0046734 | 10-15 | 87.8153 | 87.8153 | 26411669.66 | 926456.06 | 526726.79 | 26811398.93 | 56.8539 | 50.0735 | 50.0735 | >30 | 56.8539 | 50.0735 | >30 |  | 69901 | 12.1847 | 10-15
109 | Non_RAPDRP | HIRIYUR | HARIYABBE | RANGENAHALLI_66 | F09-BYADARAHALLY | RANGENAHALLI_66F09-BYADARAHALLY | 1310401907010301 | AGRI | 21.0515 | 19.8284 | 40.8799 | 106 | 0 | 245 | 5984.8 | 5803.3 | 5803.3 | 0 | 181.5 | 2000 | 363000 | 1 | 363000 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373000 |  |  | 0 | 0 | 337564.714 | 0 | 337564.714 | 35435.286 | 9.5001 | 9.5 | 7.6676e-05 | 5-10 | 90.4999 | 90.4999 | 14621196 | 1964626.12 | 1964626.59 | 14621196 | 100 | 9.5001 | 9.5001 | 5-10 | 100 | 9.5001 | 5-10 |  | 337564.714 | 9.5001 | 5-10
110 | Non_RAPDRP | HIRIYUR | AIMANGALA | MALLAPPANAHALLY_66 | F01-SALLABOMMANAHALLY | MALLAPPANAHALLY_66F01-SALLABOMMANAHALLY | 1310401911020101 | AGRI | 19.6 | 22.65 | 42.25 | 123 | 3 | 447 | 7783.3 | 7577.7 | 7577.7 | 0 | 205.6 | 2000 | 411200 | 1 | 411200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411200 |  |  | 0 | 0 | 372135.69 | 0 | 372135.69 | 39064.31 | 9.5001 | 9.5 | 7.5389e-05 | 5-10 | 90.4999 | 90.4999 | 16641338.55 | 2165997.96 | 2165997.767 | 16641339.55 | 100 | 9.5001 | 9.5001 | 5-10 | 100 | 9.5001 | 5-10 |  | 372135.69 | 9.5001 | 5-10
111 | Non_RAPDRP | HIRIYUR | AIMANGALA | MALLAPPANAHALLY_66 | F03-HARTHIKOTE | MALLAPPANAHALLY_66F03-HARTHIKOTE | 1310401911020102 | AGRI | 18.3 | 20.6 | 38.9 | 119 | 10 | 206 | 5966.3 | 5685.6 | 5685.6 | 0 | 280.7 | 2000 | 561400 | 1 | 561400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135000 | 135000 | 0 | 0 | 0 | 426400 |  |  | 0 | 0 | 367581 | 0 | 367581 | 58819 | 13.7943 | 13.79 | 0.0043246 | 10-15 | 86.2057 | 86.2057 | 9544090.15 | 2143980.7 | 2136516.7 | 9551554.15 | 99.6519 | 14.0944 | 14.0944 | 10-15 | 99.6519 | 14.0944 | 10-15 | 0 | 367581 | 13.7943 | 10-15
112 | Non_RAPDRP | HIRIYUR | AIMANGALA | MALLAPPANAHALLY_66 | F05-METIKURKE | MALLAPPANAHALLY_66F05-METIKURKE | 1310401911010101 | AGRI | 17.9 | 19.3 | 37.2 | 95 | 0 | 204 | 5698 | 5457.6 | 5457.6 | 0 | 240.4 | 2000 | 480800 | 1 | 480800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67500 | 67500 | 0 | 0 | 0 | 413300 |  |  | 0 | 0 | 358500 | 0 | 358500 | 54800 | 13.2591 | 13.26 | -0.0008662 | 10-15 | 86.7409 | 86.7409 | 4987698 | 2086470 | 2086470 | 4987698 | 100 | 13.2591 | 13.2591 | 10-15 | 100 | 13.2591 | 10-15 | 0 | 358500 | 13.2591 | 10-15
113 | Non_RAPDRP | HIRIYUR | AIMANGALA | MALLAPPANAHALLY_66 | F06-INDUSTRIAL | MALLAPPANAHALLY_66F06-INDUSTRIAL | 1310401911010102 | INDUSTRIAL | 20.5 | 21.3 | 41.8 | 2 | 27 | 0 | 2955.9 | 2778.6 | 2778.6 | 0 | 177.3 | 2000 | 354600 | 1 | 354600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85450 | 85450 | 0 | 0 | 0 | 269150 |  |  | 0 | 0 | 240399 | 0 | 240399 | 28751 | 10.6821 | 10.7 | -0.017852 | 10-15 | 89.3179 | 89.3179 | 8788921.16 | 2634286.6 | 2868510.6 | 8554697.16 | 108.8914 | 2.7406 | 2.7406 | 0-5 | 100 | 10.6821 | 10-15 |  | 240399 | 10.6821 | 10-15
114 | Non_RAPDRP | HIRIYUR | AIMANGALA | MALLAPPANAHALLY_66 | F07-G.B.HALLY | MALLAPPANAHALLY_66F07-G.B.HALLY | 1310401911010103 | NJY | 18.4 | 16.6 | 35 | 35 | 2825 | 0 | 5195.1 | 5083.5 | 5083.5 | 0 | 111.6 | 2000 | 223200 | 1 | 223200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 25000 | 0 | 0 | 0 | 198200 |  |  | 0 | 0 | 173631.1 | 0 | 173631.1 | 24568.9 | 12.396 | 12.4 | -0.0039859 | 10-15 | 87.604 | 87.604 | 35013863.72 | 1881753.1 | 1068444.1 | 35827172.72 | 56.7792 | 50.2592 | 50.2592 | >30 | 56.7792 | 50.2592 | >30 |  | 173631.1 | 12.396 | 10-15
115 | Non_RAPDRP | HIRIYUR | AIMANGALA | MALLAPPANAHALLY_66 | F04-MALLAPPANAHALLY | MALLAPPANAHALLY_66F04-MALLAPPANAHALLY | 1310401911010101 | NJY | 16.9692 | 20.46 | 37.4292 | 129 | 3281 | 0 | 2392.1 | 2272.4 | 2272.4 | 0 | 119.7 | 2000 | 239400 | 1 | 239400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28000 | 28000 | 0 | 0 | 0 | 211400 |  |  | 0 | 0 | 195987.4 | 0 | 195987.4 | 15412.6 | 7.2907 | 7.29 | 0.00072848 | 5-10 | 92.7093 | 92.7093 | 16959005.96 | 2016800.83 | 1165458.83 | 17810347.96 | 57.7875 | 46.4256 | 46.4256 | >30 | 57.7875 | 46.4256 | >30 | 0 | 195987.4 | 7.2907 | 5-10
116 | Non_RAPDRP | HIRIYUR | AIMANGALA | MALLAPPANAHALLY_66 | F08-BHOTAPPANAGUDI | MALLAPPANAHALLY_66F08-BHOTAPPANAGUDI | 1310401911010104 | AGRI | 21.1215 | 19.8984 | 41.0199 | 135 | 67 | 315 | 5445.3 | 5257.7 | 5257.7 | 0 | 187.6 | 2000 | 375200 | 1 | 375200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375200 |  |  | 0 | 0 | 339555.5 | 0 | 339555.5 | 35644.5 | 9.5001 | 9.5 | 0.00013326 | 5-10 | 90.4999 | 90.4999 | 11264818.61 | 1980539.35 | 1977829.291 | 11267527.61 | 99.8632 | 9.624 | 9.624 | 5-10 | 99.8632 | 9.624 | 5-10 |  | 339555.5 | 9.5001 | 5-10
117 | Non_RAPDRP | HIRIYUR | HARIYABBE | PD KOTE_66 | F08-ESHWARA | PD KOTE_66F08-ESHWARA | 1310401908010106 | AGRI | 15.895 | 14.992 | 30.887 | 117 | 0 | 391 | 6763.5 | 6522.5 | 6522.5 | 0 | 241 | 2000 | 482000 | 1 | 482000 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 492000 |  |  | 0 | 0 | 445260.392 | 0 | 445260.392 | 46739.608 | 9.4999 | 9.5 | -7.9675e-05 | 5-10 | 90.5001 | 90.5001 | 11089333 | 2591415.99 | 2591415.23 | 11089332.92 | 100 | 9.4999 | 9.4999 | 5-10 | 100 | 9.4999 | 5-10 |  | 445260.392 | 9.4999 | 5-10
118 | Non_RAPDRP | HIRIYUR | HARIYABBE | PD KOTE_66 | F07-BASAVESHWARA | PD KOTE_66F07-BASAVESHWARA | 1310401908010108 | AGRI | 19.5988 | 18.47 | 38.0688 | 119 | 0 | 371 | 6732.8 | 6429.7 | 6429.7 | 0 | 303.1 | 2000 | 606200 | 1 | 606200 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 616200 |  |  | 0 | 0 | 557660.488 | 0 | 557660.488 | 58539.512 | 9.5001 | 9.5 | 8.309e-05 | 5-10 | 90.4999 | 90.4999 | 17259629 | 3245583.24 | 3245584.142 | 17259628.99 | 100 | 9.5001 | 9.5001 | 5-10 | 100 | 9.5001 | 5-10 |  | 557660.488 | 9.5001 | 5-10
119 | Non_RAPDRP | HIRIYUR | HARIYABBE | PD KOTE_66 | F06-BENAKANAHLLI | PD KOTE_66F06-BENAKANAHLLI | 1310401908020301 | AGRI | 20.9 | 22.6 | 43.5 | 171 | 1 | 202 | 3046.7 | 2841.1 | 2841.1 | 0 | 205.6 | 2000 | 411200 | 1 | 411200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411200 |  |  | 0 | 0 | 361100 | 0 | 361100 | 50100 | 12.1839 | 12.18 | 0.0038521 | 10-15 | 87.8161 | 87.8161 | 2277057 | 2101602 | 2101602 | 2277057 | 100 | 12.1839 | 12.1839 | 10-15 | 100 | 12.1839 | 10-15 |  | 361100 | 12.1839 | 10-15
120 | Non_RAPDRP | HIRIYUR | R.N.PURA | K R HALLY_66 | F01-YARECHIKKENAHALLY | K R HALLY_66F01-YARECHIKKENAHALLY | 1310401912010101 | AGRI | 8.25 | 12.45 | 20.7 | 45 | 40 | 185 | 74.925 | 48.916 | 48.916 | 0 | 26.009 | 20000 | 520180 | 1 | 520180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218000 | 218000 | 0 | 0 | 0 | 302180 |  |  | 0 | 0 | 263260 | 0 | 263260 | 38920 | 12.8797 | 12.88 | -0.00025945 | 10-15 | 87.1203 | 87.1203 | 5882239.56 | 1537072.17 | 1535066.17 | 5884245.56 | 99.8695 | 12.9934 | 12.9934 | 10-15 | 99.8695 | 12.9934 | 10-15 |  | 263260 | 12.8797 | 10-15
121 | Non_RAPDRP | HIRIYUR | R.N.PURA | K R HALLY_66 | F07-BORANAKUNTE | K R HALLY_66F07-BORANAKUNTE | 1310401912020101 | AGRI | 12.5 | 14.25 | 26.75 | 62 | 0 | 319 | 86.862 | 65.97 | 65.97 | 0 | 20.892 | 20000 | 417840 | 1 | 417840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417840 |  |  | 0 | 0 | 378144.204 | 0 | 378144.204 | 39695.796 | 9.5002 | 9.5 | 0.00023837 | 5-10 | 90.4998 | 90.4998 | 11880614 | 2200798.38 | 2200799.16 | 11880613.5 | 100 | 9.5002 | 9.5002 | 5-10 | 100 | 9.5002 | 5-10 |  | 378144.204 | 9.5002 | 5-10
122 | Non_RAPDRP | HIRIYUR | R.N.PURA | K R HALLY_66 | F08-K R HALLY NJY | K R HALLY_66F08-K R HALLY NJY | 1310401912020102 | NJY | 15.25 | 7.85 | 23.1 | 32 | 1014 | 0 | 25.626 | 22.03 | #N/A | #N/A | 3.596 | 20000 | 71920 | 1 | 71920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71920 |  |  | 0 | 0 | 71847.693 | 0 | 71847.693 | 72.307 | 0.10054 | 0.1 | 0.0005381 | 0-5 | 99.8995 | 99.8995 | 9780140.53 | 685127.92 | 367802.917 | 10097465.53 | 53.6838 | 46.3701 | 46.3701 | >30 | 53.6838 | 46.3701 | >30 |  | 71847.693 | 0.10054 | 0-5
123 | RAPDRP | HIRIYUR | O&M-1 | HIRIYUR_66 | F05-HIRIYURBYPASS | HIRIYUR_66F05-HIRIYURBYPASS | 1310401902020101 | MIXED LOAD | 8.3229 | 7.8142 | 16.1371 | 119 | 17072 | 0 | 2510.105 | 2461.655 | 2461.655 | 0 | 48.45 | 20000 | 969000 | 1 | 969000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 969000 | 969000 | 0 | 0 | 0 | 870990 | 0 | 870990 | 98010 | 10.1146 | 98.79 | -88.6754 | 10-15 | 89.8854 | 89.8854 | 118962.87 | 11655350.26 | 12072307.11 | -170603.56 | 103.5774 | 6.899 | 6.899 | 5-10 | 100 | 10.1146 | 10-15 |  | 870990 | 10.1146 | 10-15 |  | RAPDRP
124 | RAPDRP | HIRIYUR | O&M-1 | HIRIYUR_66 | F06-PGCL+WW | HIRIYUR_66F06-PGCL+WW | 1310401902020301 | WATER WORKS | 1.1907 | 1.1179 | 2.3086 | 2 | 29 | 0 | 181.195 | 181.028 | 181.028 | 0 | 0.167 | 20000 | 3340 | 1 | 3340 | 0 | 0 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4540 | 3340 | 1200 | 0 | 0 | 4241 | 0 | 4241 | 299 | 6.5859 | 100 | -93.4141 | 5-10 | 93.4141 | 93.4141 | -111827 | 61115 | 95578 | -130864 | 156.3904 | -46.0907 | -46.0907 | <0 | 100 | 6.5859 | 5-10 |  | 4241 | 6.5859 | 5-10 |  | RAPDRP
125 | RAPDRP | HIRIYUR | O&M-1 | HIRIYUR_66 | F09-HULIYURROAD | HIRIYUR_66F09-HULIYURROAD | 1310401902010103 | MIXED LOAD | 14.8337 | 13.9271 | 28.7608 | 204 | 20987 | 0 | 3563.29 | 3491.729 | 3491.729 | 0 | 71.561 | 20000 | 1431220 | 1 | 1431220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176200 | 176200 | 0 | 0 | 0 | 1255020 | 1255020 | 0 | 0 | 0 | 1101001.89 | 0 | 1101001.89 | 154018.11 | 12.2722 | 99.95 | -87.6778 | 10-15 | 87.7278 | 87.7278 | 3102976.36 | 9475429.15 | 9642405.26 | 3008180.73 | 101.7622 | 10.7262 | 10.7262 | 10-15 | 100 | 12.2722 | 10-15 |  | 1101001.89 | 12.2722 | 10-15 |  | RAPDRP
1 | RAPDRP | CHALLAKERE | O&M-1 | CHALLAKERE_66 | F01-PAVAGDAROAD | CHALLAKERE_66F01-PAVAGDAROAD | 1310402906020301 | MIXED LOAD | 4.8 | 3.2 | 8 | 117 | 9680 | 0 | 3737.98 | 3672.15 | #N/A | #N/A | 65.83 | 20000 | 1316600 | 1 | 1316600 | 0 | 0 | 0 | 0 | 0 | 0 | 18357.21 | 17977.06 | 380.15 | 1200 | 0 | 456180 | 0 | 0 | 0 | 860420 | 860420 | 0 | 0 | 0 | 798030.24 | 0 | 798030.24 | 62389.76 | 7.2511 | 13.16 | -5.9089 | 5-10 | 92.7489 | 92.7489 | 5583276.53 | 8674502.1 | 5892743 | 6336518.71 | 67.9318 | 36.994 | 36.994 | >30 | 67.9318 | 36.994 | >30 |  | 798030.24 | 7.2511 | 5-10
2 | RAPDRP | CHALLAKERE | O&M-1 | CHALLAKERE_66 | F02-BANGALRE ROAD | CHALLAKERE_66F02-BANGALRE ROAD | 1310402906020101 | MIXED LOAD | 6 | 4 | 10 | 33 | 1273 | 0 | 2504.63 | 2445.92 | #N/A | #N/A | 58.71 | 20000 | 1174200 | 1 | 1174200 | 0 | 0 | 0 | 0 | 0 | 0 | 19203.09 | 18852.89 | 350.2 | 3000 | 0 | 1050600 | 0 | 0 | 0 | 123600 | 123600 | 0 | 0 | 0 | 114646.7 | 0 | 114646.7 | 8953.3 | 7.2438 | 13.65 | -6.4062 | 5-10 | 92.7562 | 92.7562 | 4060365.74 | 1210398.49 | 871913.78 | 3992785.74 | 72.0353 | 33.1828 | 33.1828 | >30 | 72.0353 | 33.1828 | >30 |  | 114646.7 | 7.2438 | 5-10
3 | RAPDRP | CHALLAKERE | O&M-1 | CHALLAKERE_66 | F07-SOMAGUDDIROAD | CHALLAKERE_66F07-SOMAGUDDIROAD | 1310402906010101 | URBAN | 2.4 | 1.6 | 4 | 58 | 6144 | 0 | 1538.102 | 1507.348 | 1507.348 | 0 | 30.754 | 20000 | 615080 | 1 | 615080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 60000 | 0 | 0 | 0 | 555080 |  |  | 0 | 0 | 522903 | 0 | 522903 | 32177 | 5.7968 | #N/A | #N/A | 5-10 | 94.2032 | 94.2032 | 4263556.4 | 5432566.39 | 2630825.33 | 4551871.6 | 48.4269 | 54.3803 | 54.3803 | >30 | 48.4269 | 54.3803 | >30 |  | 522903 | 5.7968 | 5-10 | This feeder load is shifted to F12-WATER SUPPLY (KUW) feeder
4 | RAPDRP | CHALLAKERE | O&M-1 | CHALLAKERE_66 | F08-BELLRY ROAD | CHALLAKERE_66F08-BELLRY ROAD | 1310402906010102 | MIXED LOAD | 7.2 | 4.8 | 12 | 116 | 1422 | 0 | 2430.956 | 2379.96 | #N/A | #N/A | 50.996 | 20000 | 1019920 | 1 | 1019920 | 0 | 0 | 0 | 0 | 0 | 0 | 25260.29 | 24950.56 | 309.73 | 2000 | 0 | 619460 | 0 | 0 | 0 | 400460 | 400460 | 0 | 0 | 0 | 367619.51 | 0 | 367619.51 | 32840.49 | 8.2007 | -20.43 | 28.6307 | 5-10 | 91.7993 | 91.7993 | 5979906.38 | 4013108.05 | 3376859 | 5619308.69 | 84.1457 | 22.7548 | 22.7548 | 20-30 | 84.1457 | 22.7548 | 20-30 |  | 367619.51 | 8.2007 | 5-10
5 | RAPDRP | CHALLAKERE | O&M-1 | CHALLAKERE_66 | F09-GANDHINAGARA | CHALLAKERE_66F09-GANDHINAGARA | 1310402906010103 | URBAN | 2.4 | 1.6 | 4 | 58 | 3289 | 0 | 1017.899 | 998.54 | 998.54 | 0 | 19.359 | 20000 | 387180 | 1 | 387180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387180 |  |  | 0 | 0 | 354200.7 | 0 | 354200.7 | 32979.3 | 8.5178 | #N/A | #N/A | 5-10 | 91.4822 | 91.4822 | 4626544.86 | 3751298.94 | 2001795.19 | 5036333.81 | 53.3627 | 51.1826 | 51.1826 | >30 | 53.3627 | 51.1826 | >30 |  | 354200.7 | 8.5178 | 5-10
6 | NonRAPDRP | CHALLAKERE | O&M-2 | BALENAHALLI_66 | F05-RATNAGIRI | BALENAHALLI_66F05-RATNAGIRI | 1310402907020301 | AGRI | 10.8 | 7.2 | 18 | 70 | 51 | 302 | 714.593 | 695.46 | 695.46 | 0 | 19.133 | 20000 | 382660 | 1 | 382660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382660 |  |  | 0 | 0 | 992 | 341100 | 342092 | 40568 | 10.6016 | 10.62 | -0.018422 | 10-15 | 89.3984 | 89.3984 | 1668451 | 2000130.97 | 1995774.97 | 1672807 | 99.7822 | 10.7963 | 10.7963 | 10-15 | 99.7822 | 10.7963 | 10-15 |  | 342092 | 10.6016 | 10-15 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
7 | NonRAPDRP | CHALLAKERE | O&M-2 | BALENAHALLI_66 | F06-RAAMAJOGIHALLY | BALENAHALLI_66F06-RAAMAJOGIHALLY | 1310402907020302 | AGRI | 12.6 | 8.4 | 21 | 88 | 10 | 314 | 732.69 | 713.45 | 713.45 | 0 | 19.24 | 20000 | 384800 | 1 | 384800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384800 |  |  | 0 | 0 | 451 | 347846.74 | 348297.74 | 36502.26 | 9.486 | 9.5 | -0.013966 | 5-10 | 90.514 | 90.514 | 2466948 | 2044004.89 | 2024467.826 | 2486485.59 | 99.0442 | 10.3512 | 10.3512 | 10-15 | 99.0442 | 10.3512 | 10-15 |  | 348297.74 | 9.486 | 5-10
8 | NonRAPDRP | CHALLAKERE | O&M-2 | BALENAHALLI_66 | F07-KURUDIHALLY | BALENAHALLI_66F07-KURUDIHALLY | 1310402907020303 | AGRI | 13.2 | 8.8 | 22 | 94 | 29 | 289 | 625.043 | 608.96 | 608.96 | 0 | 16.083 | 20000 | 321660 | 1 | 321660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321660 |  |  | 0 | 0 | 728 | 290410.927 | 291138.927 | 30521.073 | 9.4886 | 9.5 | -0.011387 | 5-10 | 90.5114 | 90.5114 | 2060066 | 1709604.1 | 1701417.083 | 2068252 | 99.5211 | 9.9221 | 9.9221 | 5-10 | 99.5211 | 9.9221 | 5-10 |  | 291138.927 | 9.4886 | 5-10
9 | NonRAPDRP | CHALLAKERE | O&M-2 | BALENAHALLI_66 | F08-BAALENAHALLY | BALENAHALLI_66F08-BAALENAHALLY | 1310402907020304 | AGRI | 12.6 | 8.4 | 21 | 88 | 4 | 389 | 891.666 | 870.12 | 870.12 | 0 | 21.546 | 20000 | 430920 | 1 | 430920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430920 |  |  | 0 | 0 | 213 | 389788.371 | 390001.371 | 40918.629 | 9.4956 | 9.5 | -0.004356 | 5-10 | 90.5044 | 90.5044 | 256116 | 2270874.52 | 2270028.054 | 256962 | 99.9627 | 9.5294 | 9.5294 | 5-10 | 99.9627 | 9.5294 | 5-10 |  | 390001.371 | 9.4956 | 5-10
10 | NonRAPDRP | CHALLAKERE | O&M-2 | BALENAHALLI_66 | F09-SAPTHAGIRI NJY | BALENAHALLI_66F09-SAPTHAGIRI NJY | 1310402907020305 | NJY | 9.6 | 6.4 | 16 | 18 | 1494 | 0 | 392.625 | 392.63 | 392.63 | 0 | -0.005 | 20000 | -100 | 1 | -100 | 0 | 0 | 0 | 0 | 169260 | 169260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169160 | -100 | 169260 | 0 | 0 | 147719.5 | 0 | 147719.5 | 21440.5 | 12.6747 | 12.73 | -0.055313 | 10-15 | 87.3253 | 87.3253 | 23710422 | 1595914.05 | 690926.59 | 24615409.46 | 43.2935 | 62.1938 | 62.1938 | >30 | 43.2935 | 62.1938 | >30 |  | 147719.5 | 12.6747 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
11 | NonRAPDRP | CHALLAKERE | O&M-2 | CHALLAKERE_66 | F03-DUGGAVARA | CHALLAKERE_66F03-DUGGAVARA | 1310402906020302 | AGRI | 16.2 | 10.8 | 27 | 152 | 9 | 319 | 856.059 | 835.15 | 835.15 | 0 | 20.909 | 20000 | 418180 | 1 | 418180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 25000 | 0 | 0 | 0 | 393180 |  |  | 0 | 0 | 2022 | 351800 | 353822 | 39358 | 10.0102 | 10 | 0.010173 | 10-15 | 89.9898 | 89.9898 | 1286324 | 2072837.59 | 2054161.59 | 1305000 | 99.099 | 10.821 | 10.821 | 10-15 | 99.099 | 10.821 | 10-15 |  | 353822 | 10.0102 | 10-15 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
12 | NonRAPDRP | CHALLAKERE | O&M-2 | CHALLAKERE_66 | F04-REDDIHALLY | CHALLAKERE_66F04-REDDIHALLY | 1310402906020303 | AGRI | 18.6 | 12.4 | 31 | 56 | 8 | 911 | 841.013 | 819.87 | 819.87 | 0 | 21.143 | 20000 | 422860 | 1 | 422860 | 0 | 0 | 0 | 0 | 650000 | 650000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1072860 |  |  | 0 | 0 | 1107 | 969904.201 | 971011.201 | 101848.799 | 9.4932 | 9.5 | -0.006795 | 5-10 | 90.5068 | 90.5068 | 3312017 | 5658509.49 | 5644986.31 | 3325539.76 | 99.761 | 9.7095 | 9.7095 | 5-10 | 99.761 | 9.7095 | 5-10 |  | 971011.201 | 9.4932 | 5-10
13 | NonRAPDRP | CHALLAKERE | O&M-2 | CHALLAKERE_66 | F05-SIDDAPURA | CHALLAKERE_66F05-SIDDAPURA | 1310402906020304 | AGRI | 15.6 | 10.4 | 26 | 114 | 73 | 452 | 974.371 | 956.96 | 956.96 | 0 | 17.411 | 20000 | 348220 | 1 | 348220 | 0 | 0 | 0 | 0 | 200000 | 200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548220 |  |  | 0 | 0 | 2772 | 493384.232 | 496156.232 | 52063.768 | 9.4969 | 9.5 | -0.003125 | 5-10 | 90.5031 | 90.5031 | 4716806 | 2906354.03 | 2892356.032 | 4730804.97 | 99.5184 | 9.9328 | 9.9328 | 5-10 | 99.5184 | 9.9328 | 5-10 |  | 496156.232 | 9.4969 | 5-10
14 | NonRAPDRP | CHALLAKERE | O&M-2 | CHALLAKERE_66 | F06-NANNIVALA | CHALLAKERE_66F06-NANNIVALA | 1310402906020305 | AGRI | 24.6 | 16.4 | 41 | 169 | 148 | 627 | 1212.846 | 1179.7 | 1179.7 | 0 | 33.146 | 20000 | 662920 | 1 | 662920 | 0 | 0 | 0 | 0 | 240000 | 240000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 902920 |  |  | 0 | 0 | 1839 | 815320.51 | 817159.51 | 85760.49 | 9.4981 | 9.5 | -0.0018728 | 5-10 | 90.5019 | 90.5019 | 4435098 | 4765939.36 | 4752617.161 | 4448419.27 | 99.7205 | 9.7511 | 9.7511 | 5-10 | 99.7205 | 9.7511 | 5-10 |  | 817159.51 | 9.4981 | 5-10
15 | Sharing between RAPDRP & Non_RAPDRP | CHALLAKERE | O&M-1 | CHALLAKERE_66 | F01-PAVAGADAROAD | CHALLAKERE_66F01-PAVAGADAROAD | 1310402906020301 | MIXED LOAD | 19.2 | 12.8 | 32 | 125 | 592 | 144 | 0 | 0 | 0 | 0 | 0 | 20000 | 0 | 1 | 0 | 18357.21 | 17977.06 | 380.15 | 1200 | 0 | 456180 | 0 | 0 | 0 | 0 | 200000 | 200000 | 0 | 0 | 0 | 256180 | -181642.79 | 437822.79 | 0 | 0 | 122165 | 152767.204 | 274932.204 | 18752.204 | 7.3199 | 13.16 | -5.8401 | 5-10 | 107.3199 | 107.3199 | 3296188 | 2202341.52 | 1817642.98 | 3680886.69 | 82.5323 | 11.4264 | 11.4264 | 10-15 | 82.5323 | 11.4264 | 10-15 |  | 274932.204 | -7.3199 | <0 | This feeder load is shifted to F02-BANGALORE ROAD feeder | This feeder is Mixed load feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | This feeder is Mixed load feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
16 | Sharing between RAPDRP & Non_RAPDRP | CHALLAKERE | O&M-1 | CHALLAKERE_66 | F02-BANGALORE ROAD | CHALLAKERE_66F02-BANGALORE ROAD | 1310402906020101 | MIXED LOAD | 15 | 10 | 25 | 114 | 3236 | 148 | 0 | 0 | 0 | 0 | 0 | 20000 | 0 | 1 | 0 | 19203.09 | 18852.89 | 350.2 | 3000 | 200000 | 1250600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1250600 | 19203.09 | 1231396.91 | 0 | 0 | 809341.6 | 215310.764 | 1024652.364 | 225947.636 | 18.0671 | 13.65 | 4.4171 | 15-20 | 81.9329 | 81.9329 | 8281219 | 9507245.62 | 8571901.299 | 9216563.42 | 90.1618 | 26.1279 | 26.1279 | 20-30 | 90.1618 | 26.1279 | 20-30 |  | 1024652.364 | 18.0671 | 15-20 |  | This feeder is Mixed load feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | This feeder is Mixed load feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
17 | Sharing between RAPDRP & Non_RAPDRP | CHALLAKERE | O&M-1 | CHALLAKERE_66 | F08-BELLARY ROAD | CHALLAKERE_66F08-BELLARY ROAD | 1310402906010102 | MIXED LOAD | 18 | 12 | 30 | 169 | 1904 | 171 | 0 | 0 | 0 | 0 | 0 | 20000 | 0 | 1 | 0 | 25260.29 | 24950.56 | 309.73 | 2000 | 0 | 619460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619460 | 25260.29 | 594199.71 | 0 | 0 | 307587.05 | 258315.454 | 565902.504 | 53557.496 | 8.6458 | -20.43 | 29.0758 | 5-10 | 91.3542 | 91.3542 | 6726039 | 4764879.05 | 4082757.037 | 7408161.25 | 85.6844 | 21.7238 | 21.7238 | 20-30 | 85.6844 | 21.7238 | 20-30 |  | 565902.504 | 8.6458 | 5-10
18 | NonRAPDRP | CHALLAKERE | O&M-1 | CHALLAKERE_66 | F10-AUXILARY+TOWNWATERSUPPLY(NEW) | CHALLAKERE_66F10-AUXILARY+TOWNWATERSUPPLY(NEW) | 1310402906020306 | WW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #N/A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | #DIV/0! |  | Only Auxalary Transformer connected 63KVA
19 | NonRAPDRP | CHALLAKERE | O&M-1/O&M-2 | CHALLAKERE_66 | F11-VEERADIMMANAHALLY NJY | CHALLAKERE_66F11-VEERADIMMANAHALLY NJY | 1310402906020102 | NJY | 14.4 | 9.6 | 24 | 27 | 1381 | 0 | 1348.386 | 1313.65 | 1313.65 | 0 | 34.736 | 10000 | 347360 | 1 | 347360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 337360 |  |  | 0 | 0 | 293477.7 | 0 | 293477.7 | 43882.3 | 13.0076 | 13.02 | -0.012441 | 10-15 | 86.9924 | 86.9924 | 34742350 | 3238502.5 | 1521495.03 | 36459357.47 | 46.9814 | 59.1297 | 59.1297 | >30 | 46.9814 | 59.1297 | >30 |  | 293477.7 | 13.0076 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
20 | NonRAPDRP | CHALLAKERE | CHALLAKERE_66 | CHALLAKERE_66 | F13-KHB-1 | CHALLAKERE_66F13-KHB-1 | 1310402906020307 | URBAN | 3.9 | 2.6 | 6.5 | 0 | 1 | 0 | 0 | 0 | #N/A | #N/A | 0 | 2000 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #N/A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | #DIV/0! |  | Newly commissioned Feeder, Tagging yet to be done
21 | NonRAPDRP | CHALLAKERE | CHALLAKERE_66 | CHALLAKERE_66 | F14-KHB-2 | CHALLAKERE_66F14-KHB-2 | 1310402906020308 | URBAN | 3.9 | 2.6 | 6.5 | 0 | 1 | 0 | 0 | 0 | #N/A | #N/A | 0 | 2000 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #N/A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | #DIV/0! |  | Newly commissioned Feeder, Tagging yet to be done
22 | NonRAPDRP | CHALLAKERE | D.B.HALLI | DYAVARANAHALLI_66 | F05- PURLAHALLY NJY | DYAVARANAHALLI_66F05- PURLAHALLY NJY | 1310402905010105 | NJY | 12 | 8 | 20 | 39 | 1880 | 0 | 624.954 | 617.14 | 617.14 | 0 | 7.814 | 10000 | 78140 | 1 | 78140 | 0 | 0 | 0 | 0 | 32000 | 32000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110140 |  |  | 0 | 0 | 96583 | 0 | 96583 | 13557 | 12.3089 | 12.28 | 0.02888 | 10-15 | 87.6911 | 87.6911 | 16202327 | 1708579.8 | 577853.8 | 17333053 | 33.8207 | 70.3422 | 70.3422 | >30 | 33.8207 | 70.3422 | >30 |  | 96583 | 12.3089 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
23 | NonRAPDRP | CHALLAKERE | D.B.HALLI | DYAVARANAHALLI_66 | F09-SURANAHALLI | DYAVARANAHALLI_66F09-SURANAHALLI | 1310402905020301 | AGRI | 19.2 | 12.8 | 32 | 180 | 105 | 534 | 11631 | 11385.5 | 11385.5 | 0 | 245.5 | 2000 | 491000 | 1 | 491000 | 0 | 0 | 0 | 0 | 250000 | 250000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741000 |  |  | 0 | 0 | 6772 | 663831.987 | 670603.987 | 70396.013 | 9.5001 | 9.5 | 0.00013671 | 5-10 | 90.4999 | 90.4999 | 1388218 | 3916406.78 | 3868351.582 | 1436273 | 98.773 | 10.6106 | 10.6106 | 10-15 | 98.773 | 10.6106 | 10-15 |  | 670603.987 | 9.5001 | 5-10
24 | NonRAPDRP | CHALLAKERE | D.B.HALLI | DYAVARANAHALLI_66 | F01-DEVARAMARIKUNTTE | DYAVARANAHALLI_66F01-DEVARAMARIKUNTTE | 1310402905010101 | AGRI | 15 | 10 | 25 | 111 | 2 | 453 | 894.84 | 872.87 | 872.87 | 0 | 21.97 | 20000 | 439400 | 1 | 439400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 439400 |  |  | 0 | 0 | 1908 | 395749.887 | 397657.887 | 41742.113 | 9.4998 | 9.5 | -0.00020187 | 5-10 | 90.5002 | 90.5002 | 502689 | 2334758.24 | 2330953.386 | 506494.69 | 99.837 | 9.6473 | 9.6473 | 5-10 | 99.837 | 9.6473 | 5-10 |  | 397657.887 | 9.4998 | 5-10
25 | NonRAPDRP | CHALLAKERE | P.R.PURA/D.B.HALLI | DYAVARANAHALLI_66 | F06-JAJUR NJY | DYAVARANAHALLI_66F06-JAJUR NJY | 1310402905010106 | NJY | 13.2 | 8.8 | 22 | 58 | 2605 | 0 | 1231.597 | 1207.03 | 1207.03 | 0 | 24.567 | 10000 | 245670 | 1 | 245670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 40000 | 0 | 0 | 0 | 205670 |  |  | 0 | 0 | 176411 | 0 | 176411 | 29259 | 14.2262 | 14.24 | -0.013812 | 10-15 | 85.7738 | 85.7738 | 36575153 | 1851475.68 | 899323.68 | 37527305 | 48.5733 | 58.3368 | 58.3368 | >30 | 48.5733 | 58.3368 | >30 |  | 176411 | 14.2262 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
26 | NonRAPDRP | CHALLAKERE | O&M-2 | DYAVARANAHALLI_66 | F02-DODDERI | DYAVARANAHALLI_66F02-DODDERI | 1310402905010102 | AGRI | 14.3136 | 9.5424 | 23.856 | 97 | 15 | 459 | 766.129 | 743.76 | 743.76 | 0 | 22.369 | 20000 | 447380 | 1 | 447380 | 0 | 0 | 0 | 0 | 120000 | 120000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 567380 |  |  | 0 | 0 | 221 | 511100 | 511321 | 56059 | 9.8803 | 9.87 | 0.010327 | 5-10 | 90.1197 | 90.1197 | 508384 | 2977999.59 | 2977577.59 | 508806 | 99.9858 | 9.8931 | 9.8931 | 5-10 | 99.9858 | 9.8931 | 5-10 |  | 511321 | 9.8803 | 5-10
27 | NonRAPDRP | CHALLAKERE | O&M-2 | DYAVARANAHALLI_66 | F04-KARIKERE | DYAVARANAHALLI_66F04-KARIKERE | 1310402905010104 | AGRI | 21.6 | 14.4 | 36 | 180 | 0 | 278 | 547.76 | 531.22 | 531.22 | 0 | 16.54 | 20000 | 330800 | 1 | 330800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330800 |  |  | 0 | 0 | 0 | 299373.812 | 299373.812 | 31426.188 | 9.5001 | 9.5 | 5.6832e-05 | 5-10 | 90.4999 | 90.4999 | 505551 | 1742356.25 | 1742355.525 | 505551 | 100 | 9.5001 | 9.5001 | 5-10 | 100 | 9.5001 | 5-10 |  | 299373.812 | 9.5001 | 5-10
28 | NonRAPDRP | CHALLAKERE | O&M-2 | DYAVARANAHALLI_66 | F07-BHARAMASAGARA NJY | DYAVARANAHALLI_66F07-BHARAMASAGARA NJY | 1310402905010107 | NJY | 12.6 | 8.4 | 21 | 50 | 2448 | 0 | 17543.6 | 17287 | 17287 | 0 | 256.6 | 1000 | 256600 | 1 | 256600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 100000 | 0 | 0 | 0 | 156600 |  |  | 0 | 0 | 136463.8 | 0 | 136463.8 | 20136.2 | 12.8584 | 12.86 | -0.0016347 | 10-15 | 87.1416 | 87.1416 | 30957658 | 1574153.65 | 984104.65 | 31547707 | 62.5164 | 45.5222 | 45.5222 | >30 | 62.5164 | 45.5222 | >30 |  | 136463.8 | 12.8584 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
29 | NonRAPDRP | CHALLAKERE | O&M-2 | DYAVARANAHALLI_66 | F08-RANIKERE NJY | DYAVARANAHALLI_66F08-RANIKERE NJY | 1310402905010108 | NJY | 11.4 | 7.6 | 19 | 33 | 778 | 0 | 6529.2 | 6463.2 | 6463.2 | 0 | 66 | 1000 | 66000 | 1 | 66000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66000 |  |  | 0 | 0 | 56782 | 0 | 56782 | 9218 | 13.9667 | 13.97 | -0.0033333 | 10-15 | 86.0333 | 86.0333 | 8166172 | 576775.34 | 416951.34 | 8325996 | 72.2901 | 37.8064 | 37.8064 | >30 | 72.2901 | 37.8064 | >30 |  | 56782 | 13.9667 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
30 | NonRAPDRP | CHALLAKERE | SANIKERE | KALAMARANAHALLI_66 | F01-GORALATTU | KALAMARANAHALLI_66F01-GORALATTU | 1310402904010101 | AGRI | 12 | 8 | 20 | 118 | 27 | 430 | 686.26 | 660.08 | 660.08 | 0 | 26.18 | 20000 | 523600 | 1 | 523600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523600 |  |  | 0 | 0 | 939 | 472991.286 | 473930.286 | 49669.714 | 9.4862 | 9.5 | -0.013806 | 5-10 | 90.5138 | 90.5138 | 503885 | 2764149.05 | 2761667.249 | 506367.98 | 99.9102 | 9.5675 | 9.5675 | 5-10 | 99.9102 | 9.5675 | 5-10 |  | 473930.286 | 9.4862 | 5-10
31 | NonRAPDRP | CHALLAKERE | SANIKERE | KALAMARANAHALLI_66 | F03-KALAMARANAHALLI | KALAMARANAHALLI_66F03-KALAMARANAHALLI | 1310402904010103 | AGRI | 9 | 6 | 15 | 33 | 0 | 145 | 490.526 | 463.4 | 463.4 | 0 | 27.126 | 20000 | 542520 | 1 | 542520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 350000 | 0 | 0 | 0 | 192520 |  |  | 0 | 0 | 0 | 166600 | 166600 | 25920 | 13.4635 | 13.49 | -0.026464 | 10-15 | 86.5365 | 86.5365 | 13651 | 969612 | 969612 | 13651 | 100 | 13.4635 | 13.4635 | 10-15 | 100 | 13.4635 | 10-15 |  | 166600 | 13.4635 | 10-15 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
32 | NonRAPDRP | CHALLAKERE | SANIKERE | KALAMARANAHALLI_66 | F04-BELAGERE | KALAMARANAHALLI_66F04-BELAGERE | 1310402904010104 | AGRI | 7.2 | 4.8 | 12 | 103 | 2 | 245 | 491.004 | 477.43 | 477.43 | 0 | 13.574 | 20000 | 271480 | 1 | 271480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271480 |  |  | 0 | 0 | 2 | 245742.058 | 245744.058 | 25735.942 | 9.4799 | 9.5 | -0.020133 | 5-10 | 90.5201 | 90.5201 | -63914 | 1430513.84 | 1430218.78 | -63619 | 99.9794 | 9.4985 | 9.4985 | 5-10 | 99.9794 | 9.4985 | 5-10 |  | 245744.058 | 9.4799 | 5-10
33 | NonRAPDRP | CHALLAKERE | SANIKERE | KALAMARANAHALLI_66 | F05-SIDDESHWARA-NJY | KALAMARANAHALLI_66F05-SIDDESHWARA-NJY | 1310402904010105 | NJY | 12.6 | 8.4 | 21 | 127 | 1535 | 0 | 227.543 | 221.33 | 221.33 | 0 | 6.213 | 20000 | 124260 | 1 | 124260 | 0 | 0 | 0 | 0 | 6000 | 6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130260 |  |  | 0 | 0 | 116792.4 | 0 | 116792.4 | 13467.6 | 10.339 | 10.38 | -0.040986 | 10-15 | 89.661 | 89.661 | 16185819 | 1165219.73 | 454359.73 | 16896679 | 38.9935 | 65.0381 | 65.0381 | >30 | 38.9935 | 65.0381 | >30 |  | 116792.4 | 10.339 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
34 | NonRAPDRP | CHALLAKERE | SANIKERE | KALAMARANAHALLI_66 | F07-NARAYANAPURA | KALAMARANAHALLI_66F07-NARAYANAPURA |  | AGRI | 12 | 8 | 20 | 125 | 0 | 380 | 2767.3 | 2586.4 | 2586.4 | 0 | 180.9 | 2000 | 361800 | 1 | 361800 | 0 | 0 | 0 | 0 | 90000 | 90000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451800 |  |  | 0 | 0 | 0 | 399101 | 399101 | 52699 | 11.6642 | 11.66 | 0.004232 | 10-15 | 88.3358 | 88.3358 | 624230 | 2323624 | 2322762 | 625092 | 99.9629 | 11.697 | 11.697 | 10-15 | 99.9629 | 11.697 | 10-15 |  | 399101 | 11.6642 | 10-15 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
35 | NonRAPDRP | CHALLAKERE | SANIKERE | KALAMARANAHALLI_66 | F09-SIRADARAKAPLE | KALAMARANAHALLI_66F09-SIRADARAKAPLE | 1310402904020301 | AGRI | 8.7 | 5.8 | 14.5 |  | 0 | 118 | 5619.5 | 5315.6 | 5315.6 | 0 | 303.9 | 2000 | 607800 | 1 | 607800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 450000 | 0 | 0 | 0 | 157800 | 157800 | 0 | 0 | 0 | 0 | 138400 | 138400 | 19400 | 12.294 | 46.31 | -34.016 | 10-15 | 87.706 | 87.706 | 378710 | 805488 | 805488 | 378710 | 100 | 12.294 | 12.294 | 10-15 | 100 | 12.294 | 10-15 |  | 138400 | 12.294 | 10-15 | Due to New Software issues it is not possible to revise the import export to the feeder within stipulated period input to the feeder in generated energy audit is different from the manual energy audit submitted hence there is a difference in the Loss of manual and Generated energy audit i.e, Export in the Generated energy audit is 350000 but actual and manual is 450000 hence there is a difference of -34.02% t&D loss | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
36 | NonRAPDRP | CHALLAKERE | D.B.HALLI | PRPURA_66 | F03-DODDACHELLURU | PRPURA_66F03-DODDACHELLURU | 1310402902010103 | AGRI | 16.8 | 11.2 | 28 | 169 | 13 | 720 | 680.021 | 661.24 | 661.24 | 0 | 18.781 | 40000 | 751240 | 1 | 751240 | 0 | 0 | 0 | 0 | 200000 | 200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 951240 |  |  | 0 | 0 | 164 | 858000 | 858164 | 93076 | 9.7847 | 9.8 | -0.015298 | 5-10 | 90.2153 | 90.2153 | -722274 | 4996014.72 | 4995923.72 | -722183 | 99.9982 | 9.7863 | 9.7863 | 5-10 | 99.9982 | 9.7863 | 5-10 |  | 858164 | 9.7847 | 5-10
37 | NonRAPDRP | CHALLAKERE | D.B.HALLI | PRPURA_66 | F12-CHOWLURU | PRPURA_66F12-CHOWLURU | 1310402902010102 | AGRI | 24 | 16 | 40 | 174 | 21 | 300 | 5656 | 5461.6 | 5461.6 | 0 | 194.4 | 2000 | 388800 | 1 | 388800 | 0 | 0 | 0 | 0 | 50000 | 50000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438800 |  |  | 0 | 0 | 172 | 393300 | 393472 | 45328 | 10.33 | 10.33 | -9.1158e-06 | 10-15 | 89.67 | 89.67 | 130438 | 2293161.55 | 2291764.55 | 131835 | 99.9391 | 10.3846 | 10.3846 | 10-15 | 99.9391 | 10.3846 | 10-15 |  | 393472 | 10.33 | 10-15 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
38 | NonRAPDRP | CHALLAKERE | D.B.HALLI | PRPURA_66 | F01-T.N.KOTE | PRPURA_66F01-T.N.KOTE | 1310402902010101 | AGRI | 7.2 | 4.8 | 12 | 84 | 12 | 545 | 547.541 | 530.34 | 530.34 | 0 | 17.201 | 40000 | 688040 | 1 | 688040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 688040 |  |  | 0 | 0 | 15 | 622807.657 | 622822.657 | 65217.343 | 9.4787 | 9.5 | -0.021286 | 5-10 | 90.5213 | 90.5213 | 244607 | 3624945.65 | 3624740.543 | 244813 | 99.9943 | 9.4838 | 9.4838 | 5-10 | 99.9943 | 9.4838 | 5-10 |  | 622822.657 | 9.4787 | 5-10
39 | NonRAPDRP | CHALLAKERE | P.R.PURA | PRPURA_66 | F04-MAHADEVPURA | PRPURA_66F04-MAHADEVPURA | 1310402902020301 | AGRI | 16.8 | 11.2 | 28 | 88 | 25 | 543 | 1087.777 | 1047.46 | 1047.46 | 0 | 40.317 | 20000 | 806340 | 1 | 806340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 806340 |  |  | 0 | 0 | 5429 | 704042 | 709471 | 96869 | 12.0134 | 12.02 | -0.0065813 | 10-15 | 87.9866 | 87.9866 | -350001 | 4142320.16 | 4115103.16 | -322784 | 99.343 | 12.5915 | 12.5915 | 10-15 | 99.343 | 12.5915 | 10-15 |  | 709471 | 12.0134 | 10-15 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
40 | NonRAPDRP | CHALLAKERE | P.R.PURA | PRPURA_66 | F05-P.R.PURATOWN | PRPURA_66F05-P.R.PURATOWN | 1310402902020101 | MIXED LOAD | 3 | 2 | 5 | 33 | 2770 | 45 | 121.86 | 108.74 | 108.74 | 0 | 13.12 | 20000 | 262400 | 1 | 262400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 8000 | 0 | 0 | 0 | 254400 | 254400 | 0 | 0 | 0 | 160855.15 | 58425.072 | 219280.222 | 35119.778 | 13.8049 | 16.46 | -2.6551 | 10-15 | 86.1951 | 86.1951 | 10205157 | 2149928.42 | 1839416.4 | 10515668.91 | 85.5571 | 26.254 | 26.254 | 20-30 | 85.5571 | 26.254 | 20-30 |  | 219280.222 | 13.8049 | 10-15 | Due to New Software issues it is not possible to revise the import export to the feeder within stipulated period input to the feeder in generated energy audit is different from the manual energy audit submitted hence there is a difference in the Loss of manual and Generated energy audit i.e, Export in the Generated energy audit is 0 but actual and manual is 8000 hence there is a difference of -2.66% t&D loss | This feeder is Mixed load feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | This feeder is Mixed load feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
41 | NonRAPDRP | CHALLAKERE | P.R.PURA | PRPURA_66 | F06-KYADIGUNTE | PRPURA_66F06-KYADIGUNTE | 1310402902010104 | AGRI | 16.8 | 11.2 | 28 | 97 | 39 | 437 | 7520.1 | 7254 | 7254 | 0 | 266.1 | 2000 | 532200 | 1 | 532200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532200 |  |  | 0 | 0 | 746 | 480896.065 | 481642.065 | 50557.935 | 9.4998 | 9.5 | -0.00020011 | 5-10 | 90.5002 | 90.5002 | 197994 | 2807649.77 | 2805537.228 | 200106 | 99.9248 | 9.5679 | 9.5679 | 5-10 | 99.9248 | 9.5679 | 5-10 |  | 481642.065 | 9.4998 | 5-10
42 | NonRAPDRP | CHALLAKERE | P.R.PURA | PRPURA_66 | F07-JAJUR | PRPURA_66F07-JAJUR | 1310402902020302 | AGRI | 28.2 | 18.8 | 47 | 171 | 23 | 459 | 816.769 | 794.76 | 794.76 | 0 | 22.009 | 20000 | 440180 | 1 | 440180 | 0 | 0 | 0 | 0 | 380000 | 380000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820180 |  |  | 0 | 0 | 9 | 742343.13 | 742352.13 | 77827.87 | 9.4891 | 9.5 | -0.010879 | 5-10 | 90.5109 | 90.5109 | -133697 | 4321752.5 | 4320617.831 | -132564 | 99.9737 | 9.5129 | 9.5129 | 5-10 | 99.9737 | 9.5129 | 5-10 |  | 742352.13 | 9.4891 | 5-10
43 | NonRAPDRP | CHALLAKERE | P.R.PURA | PRPURA_66 | F08-KORLAKUNTE | PRPURA_66F08-KORLAKUNTE | 1310402902020303 | AGRI | 17.4 | 11.6 | 29 | 96 | 57 | 376 | 807.332 | 807.33 | 807.33 | 0 | 0.002 | 20000 | 40 | 1 | 40 | 0 | 0 | 0 | 0 | 527329 | 527329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 527369 |  |  | 0 | 0 | 1057 | 462000 | 463057 | 64312 | 12.1949 | 12.19 | 0.0048768 | 10-15 | 87.8051 | 87.8051 | -179923 | 2703875.03 | 2701037.03 | -177085 | 99.895 | 12.287 | 12.287 | 10-15 | 99.895 | 12.287 | 10-15 |  | 463057 | 12.1949 | 10-15 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
44 | NonRAPDRP | CHALLAKERE | P.R.PURA | PRPURA_66 | F09-SIDDESWARADURGA NJY | PRPURA_66F09-SIDDESWARADURGA NJY | 1310402902010106 | NJY | 28.8 | 19.2 | 48 | 55 | 2887 | 0 | 538.223 | 525.51 | 525.51 | 0 | 12.713 | 20000 | 254260 | 1 | 254260 | 0 | 0 | 0 | 0 | 15000 | 15000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269260 |  |  | 0 | 0 | 236278.5 | 0 | 236278.5 | 32981.5 | 12.2489 | 12.22 | 0.028942 | 10-15 | 87.7511 | 87.7511 | 34689474 | 2750501.4 | 1033933.68 | 36406041.72 | 37.5907 | 67.0137 | 67.0137 | >30 | 37.5907 | 67.0137 | >30 |  | 236278.5 | 12.2489 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
45 | NonRAPDRP | CHALLAKERE | D.B.HALLI | PRPURA_66 | F10-D.B.HALLI NJY | PRPURA_66F10-D.B.HALLI NJY | 1310402902010107 | NJY | 22.2 | 14.8 | 37 | 85 | 3097 | 0 | 1276.795 | 1245.66 | 1245.66 | 0 | 31.135 | 10000 | 311350 | 1 | 311350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 95000 | 0 | 0 | 0 | 216350 |  |  | 0 | 0 | 190325 | 0 | 190325 | 26025 | 12.0291 | 12.04 | -0.010881 | 10-15 | 87.9709 | 87.9709 | 36017746 | 2089427.82 | 1443872.28 | 36663301.54 | 69.1037 | 39.2089 | 39.2089 | >30 | 69.1037 | 39.2089 | >30 |  | 190325 | 12.0291 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
46 | NonRAPDRP | CHALLAKERE | SANIKERE | SANIKERE_66 | F01-HULIKUNTE | SANIKERE_66F01-HULIKUNTE | 1310402903020301 | AGRI | 6.6 | 4.4 | 11 | 97 | 2 | 423 | 1038.531 | 1014.71 | 1014.71 | 0 | 23.821 | 20000 | 476420 | 1 | 476420 | 0 | 0 | 0 | 0 | 50000 | 50000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 526420 |  |  | 0 | 0 | 43 | 457600 | 457643 | 68777 | 13.065 | 13.06 | 0.0050431 | 10-15 | 86.935 | 86.935 | 705469 | 2663941 | 2663232 | 706178 | 99.9734 | 13.0882 | 13.0882 | 10-15 | 99.9734 | 13.0882 | 10-15 |  | 457643 | 13.065 | 10-15 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
47 | NonRAPDRP | CHALLAKERE | SANIKERE | SANIKERE_66 | F02-KAMMATHMARIKUNTE | SANIKERE_66F02-KAMMATHMARIKUNTE | 1310402903010101 | AGRI | 6 | 4 | 10 | 109 | 1 | 262 | 849.143 | 827.56 | 827.56 | 0 | 21.583 | 20000 | 431660 | 1 | 431660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 120000 | 0 | 0 | 0 | 311660 |  |  | 0 | 0 | 0 | 278600 | 278600 | 33060 | 10.6077 | 10.61 | -0.0022865 | 10-15 | 89.3923 | 89.3923 | 2868605 | 1621452 | 1621452 | 2868605 | 100 | 10.6077 | 10.6077 | 10-15 | 100 | 10.6077 | 10-15 |  | 278600 | 10.6077 | 10-15 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
48 | NonRAPDRP | CHALLAKERE | SANIKERE | SANIKERE_66 | F03-CHIKKANAHALLY | SANIKERE_66F03-CHIKKANAHALLY | 1310402903010102 | AGRI | 12 | 8 | 20 | 125 | 0 | 387 | 936.718 | 910.9 | 910.9 | 0 | 25.818 | 20000 | 516360 | 1 | 516360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 50000 | 0 | 0 | 0 | 466360 |  |  | 0 | 0 | 0 | 418400 | 418400 | 47960 | 10.2839 | 10.28 | 0.0039008 | 10-15 | 89.7161 | 89.7161 | 236775 | 2435088 | 2435088 | 236775 | 100 | 10.2839 | 10.2839 | 10-15 | 100 | 10.2839 | 10-15 |  | 418400 | 10.2839 | 10-15 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
49 | NonRAPDRP | CHALLAKERE | SANIKERE | SANIKERE_66 | F04-SANIKERE | SANIKERE_66F04-SANIKERE | 1310402903010103 | AGRI | 7.8 | 5.2 | 13 | 124 | 0 | 457 | 825.752 | 803.97 | 803.97 | 0 | 21.782 | 20000 | 435640 | 1 | 435640 | 0 | 0 | 0 | 0 | 140000 | 140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575640 |  |  | 0 | 0 | 0 | 520937 | 520937 | 54703 | 9.503 | 9.5 | 0.002988 | 5-10 | 90.497 | 90.497 | 1803635 | 3031853.89 | 3031853.357 | 1803634.57 | 100 | 9.503 | 9.503 | 5-10 | 100 | 9.503 | 5-10 |  | 520937 | 9.503 | 5-10
50 | NonRAPDRP | CHALLAKERE | SANIKERE | SANIKERE_66 | F06-HEGGERE | SANIKERE_66F06-HEGGERE | 1310402903020302 | AGRI | 6 | 4 | 10 | 80 | 0 | 263 | 678.308 | 657.22 | 657.22 | 0 | 21.088 | 20000 | 421760 | 1 | 421760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140000 | 140000 | 0 | 0 | 0 | 281760 |  |  | 0 | 0 | 0 | 255046.761 | 255046.761 | 26713.239 | 9.4808 | 9.5 | -0.019151 | 5-10 | 90.5192 | 90.5192 | 2311327 | 1484372.9 | 1484372.152 | 2311327.04 | 99.9999 | 9.4809 | 9.4809 | 5-10 | 99.9999 | 9.4809 | 5-10 |  | 255046.761 | 9.4808 | 5-10
51 | NonRAPDRP | CHALLAKERE | SANIKERE | SANIKERE_66 | F07-GOPANAHALLY | SANIKERE_66F07-GOPANAHALLY | 1310402903020303 | AGRI | 4.8 | 3.2 | 8 | 58 | 1 | 158 | 586.149 | 563.08 | 563.08 | 0 | 23.069 | 20000 | 461380 | 1 | 461380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270000 | 270000 | 0 | 0 | 0 | 191380 |  |  | 0 | 0 | 0 | 173126.145 | 173126.145 | 18253.855 | 9.538 | 9.5 | 0.038016 | 5-10 | 90.462 | 90.462 | 1159307 | 1007593.99 | 1007594.171 | 1159307 | 100 | 9.538 | 9.538 | 5-10 | 100 | 9.538 | 5-10 |  | 173126.145 | 9.538 | 5-10
52 | NonRAPDRP | CHALLAKERE | SANIKERE | SANIKERE_66 | F12-UJJANI NJY | SANIKERE_66F12-UJJANI NJY | 1310402903020304 | NJY | 21.6 | 14.4 | 36 | 91 | 1997 | 0 | 3876.2 | 3789.4 | 3789.4 | 0 | 86.8 | 10000 | 868000 | 1 | 868000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540000 | 540000 | 0 | 0 | 0 | 328000 |  |  | 0 | 0 | 290387.8 | 0 | 290387.8 | 37612.2 | 11.4671 | 11.47 | -0.0028659 | 10-15 | 88.5329 | 88.5329 | 27561442 | 3034725.7 | 1854493.7 | 28741674 | 61.1091 | 45.8984 | 45.8984 | >30 | 61.1091 | 45.8984 | >30 |  | 290387.8 | 11.4671 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
53 | NonRAPDRP | CHALLAKERE | SANIKERE | SANIKERE_66 | F10-KAPARAHALLY NJY | SANIKERE_66F10-KAPARAHALLY NJY | 1310402903020305 | NJY | 4.8 | 3.2 | 8 | 36 | 1311 | 0 | 8103.4 | 7991.3 | 7991.3 | 0 | 112.1 | 1000 | 112100 | 1 | 112100 | 0 | 0 | 0 | 0 | 8000 | 8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120100 |  |  | 0 | 0 | 104260 | 0 | 104260 | 15840 | 13.189 | 13.19 | -0.00099084 | 10-15 | 86.811 | 86.811 | 22279448 | 1062024.99 | 429346.36 | 22912126.63 | 40.4271 | 64.9048 | 64.9048 | >30 | 40.4271 | 64.9048 | >30 |  | 104260 | 13.189 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
54 | NonRAPDRP | CHALLAKERE | SANIKERE | SANIKERE_66 | F09-BHAGAVANTHA NJY | SANIKERE_66F09-BHAGAVANTHA NJY | 1310402903020306 | NJY | 6 | 4 | 10 | 60 | 1946 | 0 | 1352.139 | 1319.62 | 1319.62 | 0 | 32.519 | 2000 | 65038 | 1 | 65038 | 0 | 0 | 0 | 0 | 100000 | 100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165038 |  |  | 0 | 0 | 144334.8 | 0 | 144334.8 | 20703.2 | 12.5445 | 12.54 | 0.0045049 | 10-15 | 87.4555 | 87.4555 | 25911210 | 1478282.2 | 816228.89 | 26573263.31 | 55.2147 | 51.7117 | 51.7117 | >30 | 55.2147 | 51.7117 | >30 |  | 144334.8 | 12.5445 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
55 | NonRAPDRP | CHALLAKERE | D.B.HALLI | DYAVARANAHALLI_66 | F12-MATSAMUDRA | DYAVARANAHALLI_66F12-MATSAMUDRA | 1310402905020303 | AGRI | 12 | 8 | 20 | 58 | 3 | 187 | 9859.4 | 9647.9 | 9647.9 | 0 | 211.5 | 2000 | 423000 | 1 | 423000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 200000 | 0 | 0 | 0 | 223000 |  |  | 0 | 0 | 0 | 201815.36 | 201815.36 | 21184.64 | 9.4998 | 9.5 | -0.00016143 | 5-10 | 90.5002 | 90.5002 | 614613 | 1174564.8 | 1174565.393 | 614613 | 100.0001 | 9.4998 | 9.4998 | 5-10 | 100 | 9.4998 | 5-10 |  | 201815.36 | 9.4998 | 5-10
56 | NonRAPDRP | CHALLAKERE | O&M-2 | DYAVARANAHALLI_66 | F03-MEERASABHIHALLY | DYAVARANAHALLI_66F03-MEERASABHIHALLY | 1310402905010103 | AGRI | 7.8 | 5.2 | 13 | 58 | 3 | 175 | 1774.1 | 1771.7 | 1771.7 | 0 | 2.4 | 20000 | 48000 | 1 | 48000 | 0 | 0 | 0 | 0 | 160000 | 160000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208000 |  |  | 0 | 0 | 6 | 188234.14 | 188240.14 | 19759.86 | 9.4999 | 9.5 | -6.7308e-05 | 5-10 | 90.5001 | 90.5001 | 541756 | 1099745.32 | 1095708.646 | 545793 | 99.6329 | 9.8321 | 9.8321 | 5-10 | 99.6329 | 9.8321 | 5-10 |  | 188240.14 | 9.4999 | 5-10
57 | NonRAPDRP | CHALLAKERE | O&M-2 | VISHWESHWARAPURA_66 | F01-V V PURA | VISHWESHWARAPURA_66F01-V V PURA | 1310402909010101 | AGRI | 6 | 4 | 10 | 58 | 0 | 215 | 9766.1 | 9494.9 | 9494.9 | 0 | 271.2 | 2000 | 542400 | 1 | 542400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 250000 | 0 | 0 | 0 | 292400 |  |  | 0 | 0 | 124 | 235700 | 235824 | 56576 | 19.3488 | 19.35 | -0.0011628 | 15-20 | 80.6512 | 80.6512 | 632694 | 1373007.77 | 1372748.77 | 632953 | 99.9811 | 19.3641 | 19.3641 | 15-20 | 99.9811 | 19.3641 | 15-20 |  | 235824 | 19.3488 | 15-20 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
58 | NonRAPDRP | CHALLAKERE | P.R.PURA/D.B.HALLI | PRPURA_66 | F15-HULLIKATTE NJY | PRPURA_66F15-HULLIKATTE NJY | 1310402902020304 | NJY | 7.92 | 5.28 | 13.2 | 7 | 3722 | 0 | 10380.2 | 10211.1 | 10211.1 | 0 | 169.1 | 2000 | 338200 | 1 | 338200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 125000 | 0 | 0 | 0 | 213200 |  |  | 0 | 0 | 186752.1 | 0 | 186752.1 | 26447.9 | 12.4052 | 12.41 | -0.0047936 | 10-15 | 87.5948 | 87.5948 | 37897401 | 2097484.74 | 1501646.74 | 38493239 | 71.5927 | 37.2885 | 37.2885 | >30 | 71.5927 | 37.2885 | >30 |  | 186752.1 | 12.4052 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
59 | NonRAPDRP | CHALLAKERE | O&M-2 | VISHWESHWARAPURA_66 | F02-RANGAVANAHALLY NJY | VISHWESHWARAPURA_66F02-RANGAVANAHALLY NJY | 1310402909010102 | NJY | 4.8 | 3.2 | 8 | 58 | 1534 | 0 | 3547.9 | 3480.1 | 3480.1 | 0 | 67.8 | 2000 | 135600 | 1 | 135600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135600 |  |  | 0 | 0 | 117898 | 0 | 117898 | 17702 | 13.0546 | 13.05 | 0.0045723 | 10-15 | 86.9454 | 86.9454 | 15994856 | 1184257.27 | 711454.64 | 16467658.63 | 60.076 | 47.7666 | 47.7666 | >30 | 60.076 | 47.7666 | >30 |  | 117898 | 13.0546 | 10-15 |  | Due to Electromechanical meters present in the feeder and as well as some water supply installations reading not properly done. | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder | Replacement of Electromechanical meters by Electro static meters, Proper & in time reading of all installations & proposed LT reaconductoring of all villages covered under this feeder
60 | NonRAPDRP | CHALLAKERE | P.R.PURA | PRPURA_66 | F14-P.GOWRIPURA | PRPURA_66F14-P.GOWRIPURA | 1310402902020305 | AGRI | 5.7 | 3.8 | 9.5 | 20 | 110 | 193 | 7300.2 | 7022 | 7022 | 0 | 278.2 | 2000 | 556400 | 1 | 556400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 200000 | 0 | 0 | 0 | 356400 |  |  | 0 | 0 | 3365 | 293300 | 296665 | 59735 | 16.7607 | 16.76 | 0.00066218 | 15-20 | 83.2393 | 83.2393 | 81239 | 1747197.34 | 1743386.34 | 85050 | 99.7819 | 16.9422 | 16.9422 | 15-20 | 99.7819 | 16.9422 | 15-20 |  | 296665 | 16.7607 | 15-20 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
61 | NonRAPDRP | CHALLAKERE | P.R.PURA | PRPURA_66 | F16-PAGADALABANDE | PRPURA_66F16-PAGADALABANDE | 1310402902020306 | AGRI | 6.918 | 4.612 | 11.53 | 9 | 25 | 116 | 988.956 | 963.9 | 963.9 | 0 | 25.056 | 20000 | 501120 | 1 | 501120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 300000 | 0 | 0 | 0 | 201120 |  |  | 0 | 0 | 943 | 180998.394 | 181941.394 | 19178.606 | 9.5359 | 9.5 | 0.035902 | 5-10 | 90.4641 | 90.4641 | 215665 | 1063498.94 | 1063660.625 | 215503 | 100.0152 | 9.5221 | 9.5221 | 5-10 | 100 | 9.5359 | 5-10 |  | 181941.394 | 9.5359 | 5-10
62 | NonRAPDRP | CHALLAKERE | D.B.HALLI | PRPURA_66 | F02-GOSIKERE | PRPURA_66F02-GOSIKERE | 1310402902010108 | AGRI | 19.2 | 12.8 | 32 | 22 | 74 | 564 | 576.655 | 560.02 | 560.02 | 0 | 16.635 | 40000 | 665400 | 1 | 665400 | 0 | 0 | 0 | 0 | 60000 | 60000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725400 |  |  | 0 | 0 | 3985 | 652500.671 | 656485.671 | 68914.329 | 9.5002 | 9.5 | 0.00018321 | 5-10 | 90.4998 | 90.4998 | 456534 | 3838566.24 | 3815347.973 | 479752 | 99.3951 | 10.0476 | 10.0476 | 10-15 | 99.3951 | 10.0476 | 10-15 |  | 656485.671 | 9.5002 | 5-10
63 | NonRAPDRP | CHALLAKERE | D.B.HALLI | PRPURA_66 | F13-C.B.HALLI | PRPURA_66F13-C.B.HALLI | 1310402902010109 | AGRI | 15 | 10 | 25 | 25 | 4 | 345 | 7351.9 | 7061.3 | 7061.3 | 0 | 290.6 | 2000 | 581200 | 1 | 581200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130000 | 130000 | 0 | 0 | 0 | 451200 |  |  | 0 | 0 | 0 | 408335.588 | 408335.588 | 42864.412 | 9.5001 | 9.5 | 9.1312e-05 | 5-10 | 90.4999 | 90.4999 | -18456 | 2376513.44 | 2376512.975 | -18456 | 100 | 9.5001 | 9.5001 | 5-10 | 100 | 9.5001 | 5-10 |  | 408335.588 | 9.5001 | 5-10
64 | NonRAPDRP | CHALLAKERE | D.B.HALLI | DYAVARANAHALLI_66 | F10-VADERAHALLI | DYAVARANAHALLI_66F10-VADERAHALLI | 1310402905020302 | AGRI | 18 | 12 | 30 | 28 | 26 | 429 | 11456.4 | 11215.7 | 11215.7 | 0 | 240.7 | 2000 | 481400 | 1 | 481400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481400 |  |  | 0 | 0 | 416 | 435249.892 | 435665.892 | 45734.108 | 9.5002 | 9.5 | 0.00023016 | 5-10 | 90.4998 | 90.4998 | -216913 | 2538366.7 | 2537997.405 | -216543.01 | 99.9855 | 9.5134 | 9.5134 | 5-10 | 99.9855 | 9.5134 | 5-10 |  | 435665.892 | 9.5002 | 5-10
65 | NonRAPDRP | CHALLAKERE | D.B.HALLI | DYAVARANAHALLI_66 | F11-CHANNAMMANAGATHI HALLI | DYAVARANAHALLI_66F11-CHANNAMMANAGATHI HALLI | 1310402905020304 | AGRI | 16.8 | 11.2 | 28 | 15 | 1 | 283 | 7190.7 | 7005.5 | 7005.5 | 0 | 185.2 | 2000 | 370400 | 1 | 370400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370400 |  |  | 0 | 0 | 0 | 316500 | 316500 | 53900 | 14.5518 | 14.55 | 0.0018359 | 10-15 | 85.4482 | 85.4482 | 319639 | 1842030 | 1842030 | 319639 | 100 | 14.5518 | 14.5518 | 10-15 | 100 | 14.5518 | 10-15 |  | 316500 | 14.5518 | 10-15 |  | This feeder is Agri feeder At present total sanction load of IP Sets is less compare to actual load in the feeder i.e the reason per HP consumption is more but system taken Sub-division avarage by default then automatically feeder loss is more. | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | 1.Regullarisation of Unauthorised IP Sets in the Feeder 2. Proposed to execute HVDS in the Feeder 3.Proposed to Reconductoring of both HT and LT Lines in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load
66 | NonRAPDRP | CHALLAKERE | O&M-1 | CHALLAKERE_66 | F12-WATER SUPPLY (KUW) | CHALLAKERE_66F12-WATER SUPPLY (KUW) | 1310402906010106 | WW | 4.8 | 3.2 | 8 | 2 | 2 | 0 | 358.426 | 353.46 | 353.46 | 0 | 4.966 | 10000 | 49660 | 1 | 49660 | 0 | 0 | 0 | 0 | 60000 | 60000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109660 | 49660 | 60000 | 0 | 0 | 103350 | 0 | 103350 | 6310 | 5.7541 | -108.12 | 113.8741 | 5-10 | 94.2459 | 94.2459 | 0 | 945425 | 751057 | 194368 | 79.4412 | 25.13 | 25.13 | 20-30 | 79.4412 | 25.13 | 20-30 |  | 103350 | 5.7541 | 5-10 | Due to New Software issues it is not possible to revise the import export to the feeder within stipulated period input to the feeder in generated energy audit is different from the manual energy audit submitted hence there is a difference in the Loss of manual and Generated energy audit i.e, Import t in the Generated energy audit is 0 but actual and manual is 60000 hence there is a difference of 113.87% t&D loss
1 | Non_RAPDRP | MOLAKALMURU | B.G.kere | BGKERE_66 | F01-GOWRASAMUDRA | BGKERE_66F01-GOWRASAMUDRA | 1310403904010101 | AGRI | 16.2723 | 9.88 | 26.1523 | 40 | 2 | 237 | 669.109 | 649.197 | 649.197 | 0 | 19.912 | 20000 | 398240 | 1 | 398240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398240 |  |  | 0 | 0 | 272158 | 0 | 272158 | 126082 | 31.6598 | 31.66 | -0.00019687 | >30 | 68.3402 | 68.3402 | 4837038 | 1584564.98 | 1584132.98 | 4837471.82 | 99.9727 | 31.6784 | 31.6784 | >30 | 99.9727 | 31.6784 | >30 |  | 272158 | 31.6598 | >30 | Assessed Energy | 01.Unauthourised IP sets 02.Most of the ipset has more load capacity than sanctioned load in the field
2 | Non_RAPDRP | MOLAKALMURU | B.G.kere | BGKERE_66 | F02-BGKERE | BGKERE_66F02-BGKERE | 1310403904010102 | AGRI | 18.03 | 10.64 | 28.67 | 183 | 5 | 469 | 628.438 | 617.738 | 617.738 | 0 | 10.7 | 30000 | 321000 | 1 | 321000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321000 |  |  | 0 | 0 | 290505.712 | 0 | 290505.712 | 30494.288 | 9.4998 | 9.5 | -0.00022181 | 5-10 | 90.5002 | 90.5002 | 8419801 | 1691837.26 | 1691442.238 | 8420196 | 99.9767 | 9.5209 | 9.5209 | 5-10 | 99.9767 | 9.5209 | 5-10 |  | 290505.712 | 9.4998 | 5-10
3 | Non_RAPDRP | MOLAKALMURU | B.G.kere | BGKERE_66 | F03-ABBENAHALLI | BGKERE_66F03-ABBENAHALLI | 1310403904010103 | AGRI | 16.74 | 10.26 | 27 | 19 | 6 | 411 | 941.875 | 916.946 | 916.946 | 0 | 24.929 | 20000 | 498580 | 1 | 498580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 498580 |  |  | 0 | 0 | 451214.511 | 0 | 451214.511 | 47365.489 | 9.5001 | 9.5 | 7.8022e-05 | 5-10 | 90.4999 | 90.4999 | 6755685.6 | 2626755.27 | 2626727.305 | 6755712.96 | 99.9989 | 9.501 | 9.501 | 5-10 | 99.9989 | 9.501 | 5-10 |  | 451214.511 | 9.5001 | 5-10
4 | Non_RAPDRP | MOLAKALMURU | B.G.kere | BGKERE_66 | F04-SURAMMANAHALLI | BGKERE_66F04-SURAMMANAHALLI | 1310403904010104 | AGRI | 17.46 | 10.64 | 28.1 | 119 | 36 | 520 | 912.399 | 889.446 | 889.446 | 0 | 22.953 | 20000 | 459060 | 1 | 459060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459060 |  |  | 0 | 0 | 415450.037 | 0 | 415450.037 | 43609.963 | 9.4998 | 9.5 | -0.00016055 | 5-10 | 90.5002 | 90.5002 | 11227681 | 2424782.44 | 2422881.06 | 11229584 | 99.9216 | 9.5708 | 9.5708 | 5-10 | 99.9216 | 9.5708 | 5-10 |  | 415450.037 | 9.4998 | 5-10
5 | Non_RAPDRP | MOLAKALMURU | B.G.kere | BGKERE_66 | F05-NJY-MUSTELLAGUMMI | BGKERE_66F05-NJY-MUSTELLAGUMMI | 1310403904010100 | NJY | 17.98 | 11.02 | 29 | 31 | 1636 | 0 | 27.595 | 16.79 | 16.79 | 0 | 10.805 | 20000 | 216100 | 1 | 216100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216100 |  |  | 0 | 0 | 185480 | 0 | 185480 | 30620 | 14.1694 | 14.17 | -0.00063397 | 10-15 | 85.8306 | 85.8306 | 34237951 | 1747165.96 | 726516.32 | 35258600.64 | 41.5826 | 64.3094 | 64.3094 | >30 | 41.5826 | 64.3094 | >30 |  | 185480 | 14.1694 | 10-15
6 | Non_RAPDRP | MOLAKALMURU | B.G.kere | BGKERE_66 | F07-KONDALAHALLY | BGKERE_66F07-KONDALAHALLY | 1310403904010100 | NJY | 13.843 | 8.36 | 22.203 | 74 | 2807 | 0 | 143.322 | 117.915 | 117.915 | 0 | 25.407 | 10000 | 254070 | 1 | 254070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103562 | 357632 |  |  | 0 | 0 | 305616.9 | 0 | 305616.9 | 52015.1 | 14.5443 | 14.54 | 0.0043081 | 10-15 | 85.4557 | 85.4557 | 30427999 | 2979484.46 | 2352744.93 | 31054738.53 | 78.9648 | 32.5201 | 32.5201 | >30 | 78.9648 | 32.5201 | >30 |  | 305616.9 | 14.5443 | 10-15
7 | Non_RAPDRP | MOLAKALMURU | B.G.kere | BGKERE_66 | F08-RAVALAKUNTE | BGKERE_66F08-RAVALAKUNTE | 1310403904020300 | AGRI | 0.25 | 0 | 0.25 | 141 | 1 | 177 | 75.071 | 57.937 | 57.937 | 0 | 17.134 | 20000 | 342680 | 1 | 342680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342680 |  |  | 0 | 0 | 269079 | 0 | 269079 | 73601 | 21.4781 | 21.48 | -0.0019447 | 20-30 | 78.5219 | 78.5219 | 2377425 | 1566235.54 | 1566232.54 | 2377428 | 99.9998 | 21.4782 | 21.4782 | 20-30 | 99.9998 | 21.4782 | 20-30 |  | 269079 | 21.4781 | 20-30 | Assessed Energy | 01.Unauthourised IP sets 02.Most of the ipset has more load capacity than sanctioned load in the field
8 | Non_RAPDRP | MOLAKALMURU | B.G.kere | BGKERE_66 | F10-MOGHALAHALLY NJY | BGKERE_66F10-MOGHALAHALLY NJY | 1310403904020300 | NJY | 12.51 | 7.6 | 20.11 | 41 | 1349 | 0 | 343.586 | 338.683 | 338.683 | 0 | 4.903 | 20000 | 98060 | 1 | 98060 | 0 | 0 | 0 | 0 | 69954 | 69954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168014 |  |  | 0 | 0 | 153483.3 | 0 | 153483.3 | 14530.7 | 8.6485 | 8.65 | -0.0014945 | 5-10 | 91.3515 | 91.3515 | 12336134 | 1474721.53 | 973669.89 | 12837185.64 | 66.024 | 39.6861 | 39.6861 | >30 | 66.024 | 39.6861 | >30 |  | 153483.3 | 8.6485 | 5-10
9 | Non_RAPDRP | MOLAKALMURU | MOLAKALMURU | HANAGAL_66 | F01-GUNDLURU | HANAGAL_66F01-GUNDLURU | 1310403906020300 | AGRI | 11.78 | 7.22 | 19 | 127 | 1 | 146 | 410.951 | 393.14 | 393.14 | 0 | 17.811 | 20000 | 356220 | 1 | 356220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356220 |  |  | 0 | 0 | 222746 | 0 | 222746 | 133474 | 37.4695 | 37.47 | -0.00045871 | >30 | 62.5305 | 62.5305 | 2908316 | 1303915 | 1303899 | 2908332 | 99.9988 | 37.4703 | 37.4703 | >30 | 99.9988 | 37.4703 | >30 |  | 222746 | 37.4695 | >30 | Assessed Energy | 01.Unauthourised IP sets 02.Most of the ipset has more load capacity than sanctioned load in the field
10 | Non_RAPDRP | MOLAKALMURU | MOLAKALMURU | HANAGAL_66 | F02-MOLKALMURU | HANAGAL_66F02-MOLKALMURU | 1310403906020300 | MIXED LOAD | 12.644 | 7.6 | 20.244 | 111 | 6262 | 133 | 1747.985 | 1709.823 | 1709.823 | 0 | 38.162 | 20000 | 763240 | 1 | 763240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763240 |  |  | 0 | 0 | 620694.332 | 0 | 620694.332 | 142545.668 | 18.6764 | 18.68 | -0.0036114 | 15-20 | 81.3236 | 81.3236 | 12307026.96 | 5966532.4 | 5149117.101 | 13124441.86 | 86.3 | 29.8177 | 29.8177 | 20-30 | 86.3 | 29.8177 | 20-30 | 0 | 620694.332 | 18.6764 | 15-20 | Assessed Energy | Due to urban mixed load feeder power supply is given to 133 ip sets more than 7 hours
11 | Non_RAPDRP | MOLAKALMURU | MOLAKALMURU | HANAGAL_66 | F03-BYRAPURA | HANAGAL_66F03-BYRAPURA | 1310403906020300 | AGRI | 11.16 | 6.84 | 18 | 79 | 0 | 32 | 469.925 | 468.078 | 468.078 | 0 | 1.847 | 20000 | 36940 | 1 | 36940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36940 |  |  | 0 | 0 | 33430.652 | 0 | 33430.652 | 3509.348 | 9.5001 | 9.5 | 0.00012994 | 5-10 | 90.4999 | 90.4999 | -38571 | 194566.405 | 194566.405 | -38570.98 | 100 | 9.5001 | 9.5001 | 5-10 | 100 | 9.5001 | 5-10 |  | 33430.652 | 9.5001 | 5-10
12 | Non_RAPDRP | MOLAKALMURU | MOLAKALMURU | HANAGAL_66 | F04-HANGAL | HANAGAL_66F04-HANGAL | 1310403906020300 | AGRI | 11.982 | 7.22 | 19.202 | 36 | 0 | 191 | 301.437 | 293.996 | 293.996 | 0 | 7.441 | 20000 | 148820 | 1 | 148820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148820 |  |  | 0 | 0 | 134682.08 | 0 | 134682.08 | 14137.92 | 9.5 | 9.5 | 1.3439e-05 | 5-10 | 90.5 | 90.5 | 4837890 | 783850.22 | 783849.716 | 4837890.05 | 99.9999 | 9.5001 | 9.5001 | 5-10 | 99.9999 | 9.5001 | 5-10 |  | 134682.08 | 9.5 | 5-10
13 | Non_RAPDRP | MOLAKALMURU | MOLAKALMURU | HANAGAL_66 | F05-MATADAJOGIHALLY | HANAGAL_66F05-MATADAJOGIHALLY | 1310403906010100 | AGRI | 17.47 | 9.88 | 27.35 | 114 | 0 | 299 | 771.373 | 751.565 | 751.565 | 0 | 19.808 | 20000 | 396160 | 1 | 396160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396160 |  |  | 0 | 0 | 358524.892 | 0 | 358524.892 | 37635.108 | 9.5 | 9.5 | -2.3223e-05 | 5-10 | 90.5 | 90.5 | 6634626 | 2086615.01 | 2086614.968 | 6634626 | 100 | 9.5 | 9.5 | 5-10 | 100 | 9.5 | 5-10 |  | 358524.892 | 9.5 | 5-10
14 | Non_RAPDRP | MOLAKALMURU | MOLAKALMURU | HANAGAL_66 | F06-TUKURLAHALLI | HANAGAL_66F06-TUKURLAHALLI | 1310403906010100 | AGRI | 23.56 | 14.44 | 38 | 30 | 16 | 509 | 337.716 | 319.228 | 319.228 | 0 | 18.488 | 20000 | 369760 | 1 | 369760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369760 |  |  | 0 | 0 | 334634.48 | 0 | 334634.48 | 35125.52 | 9.4995 | 9.5 | -0.00045435 | 5-10 | 90.5005 | 90.5005 | 6577696 | 1953431.36 | 1946812.829 | 6584314.9 | 99.6612 | 9.8062 | 9.8062 | 5-10 | 99.6612 | 9.8062 | 5-10 |  | 334634.48 | 9.4995 | 5-10
15 | Non_RAPDRP | MOLAKALMURU | MOLAKALMURU | HANAGAL_66 | F07-KONASAGARA | HANAGAL_66F07-KONASAGARA | 1310403906010100 | AGRI | 14.26 | 8.74 | 23 | 0 | 0 | 0 | 266.989 | 266.989 | #N/A | #N/A | 0 | 20000 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #N/A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | #DIV/0! |  | Idle Feeder
16 | Non_RAPDRP | MOLAKALMURU | MOLAKALMURU | HANAGAL_66 | F08-MARLAHALLI | HANAGAL_66F08-MARLAHALLI | 1310403906010100 | AGRI | 13.12 | 7.98 | 21.1 | 67 | 0 | 316 | 548.494 | 536.765 | 536.765 | 0 | 11.729 | 20000 | 234580 | 1 | 234580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234580 |  |  | 0 | 0 | 212295.978 | 0 | 212295.978 | 22284.022 | 9.4995 | 9.5 | -0.00045954 | 5-10 | 90.5005 | 90.5005 | 7117871 | 1235829.75 | 1235562.393 | 7118139 | 99.9784 | 9.5191 | 9.5191 | 5-10 | 99.9784 | 9.5191 | 5-10 |  | 212295.978 | 9.4995 | 5-10
17 | Non_RAPDRP | MOLAKALMURU | MOLAKALMURU | HANAGAL_66 | F09-RDPDAM | HANAGAL_66F09-RDPDAM | 1310403906020300 | WATER WORKS | 9.5 | 0 | 9.5 | 2 | 1 | 0 | 8.885 | 6.995 | 6.995 | 0 | 1.89 | 10000 | 18900 | 1 | 18900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18900 |  |  | 0 | 0 | 13954 | 0 | 13954 | 4946 | 26.1693 | 26.17 | -0.00068783 | 20-30 | 73.8307 | 73.8307 | 0 | 96977 | 0 | 96977 | 0 | 100 | 100 | >30 | 0 | 100 | >30 |  | 13954 | 26.1693 | 20-30 | Assessed Energy | Due to line trouble load shifted on F04 hanagal feeder
18 | Non_RAPDRP | MOLAKALMURU | MOLAKALMURU | HANAGAL_66 | F10-HANAGAL-NJY | HANAGAL_66F10-HANAGAL-NJY | 1310403906020300 | NJY | 13.64 | 8.36 | 22 | 62 | 1484 | 0 | 51.428 | 32.539 | 32.539 | 0 | 18.889 | 10000 | 188890 | 1 | 188890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188890 |  |  | 0 | 0 | 162651 | 0 | 162651 | 26239 | 13.8912 | 13.89 | 0.0011536 | 10-15 | 86.1088 | 86.1088 | 27515664 | 1543896.95 | 734603.08 | 28324957.87 | 47.5811 | 59.0285 | 59.0285 | >30 | 47.5811 | 59.0285 | >30 |  | 162651 | 13.8912 | 10-15
19 | Non_RAPDRP | MOLAKALMURU | MOLAKALMURU | HANAGAL_66 | F11-RAYAPURA NJY | HANAGAL_66F11-RAYAPURA NJY | 1310403906010100 | NJY | 17.98 | 11.02 | 29 | 164 | 3057 | 0 | 128.59 | 84.302 | 84.302 | 0 | 44.288 | 10000 | 442880 | 1 | 442880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 442880 |  |  | 0 | 0 | 387455.45 | 0 | 387455.45 | 55424.55 | 12.5146 | 12.51 | 0.0045751 | 10-15 | 87.4854 | 87.4854 | 51459628 | 3716570.12 | 2030662.7 | 53145535.42 | 54.6381 | 52.1996 | 52.1996 | >30 | 54.6381 | 52.1996 | >30 |  | 387455.45 | 12.5146 | 10-15
20 | Non_RAPDRP | MOLAKALMURU | Nagasamudra | NAGASAMUDRA_66 | F01-ASHOKSIDDAPURA | NAGASAMUDRA_66F01-ASHOKSIDDAPURA | 1310403902010100 | AGRI | 0 | 0 | 0 | 0 | 0 | 0 | 435.454 | 435.454 | #N/A | #N/A | 0 | 20000 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | -1298800 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | #DIV/0! |  | Idle Feeder
21 | Non_RAPDRP | MOLAKALMURU | Nagasamudra | NAGASAMUDRA_66 | F02-NAGASAMUDRA | NAGASAMUDRA_66F02-NAGASAMUDRA | 1310403902010100 | AGRI | 11.16 | 6.84 | 18 | 40 | 1 | 157 | 196.497 | 191.999 | 191.999 | 0 | 4.498 | 20000 | 89960 | 1 | 89960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89960 |  |  | 0 | 0 | 81414.144 | 0 | 81414.144 | 8545.856 | 9.4996 | 9.5 | -0.00038239 | 5-10 | 90.5004 | 90.5004 | 2084426 | 474114.995 | 474106.995 | 2084434.02 | 99.9983 | 9.5011 | 9.5011 | 5-10 | 99.9983 | 9.5011 | 5-10 |  | 81414.144 | 9.4996 | 5-10
22 | Non_RAPDRP | MOLAKALMURU | Nagasamudra | NAGASAMUDRA_66 | F03-AMAKUNDI | NAGASAMUDRA_66F03-AMAKUNDI | 1310403902010100 | AGRI | 11.96 | 7.22 | 19.18 | 174 | 2 | 451 | 237.81 | 220.971 | 220.971 | 0 | 16.839 | 20000 | 336780 | 1 | 336780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336780 |  |  | 0 | 0 | 304787.073 | 0 | 304787.073 | 31992.927 | 9.4997 | 9.5 | -0.0003483 | 5-10 | 90.5003 | 90.5003 | 7189270 | 1774283.764 | 1773940.676 | 7189613.45 | 99.9807 | 9.5172 | 9.5172 | 5-10 | 99.9807 | 9.5172 | 5-10 |  | 304787.073 | 9.4997 | 5-10
23 | Non_RAPDRP | MOLAKALMURU | Nagasamudra | NAGASAMUDRA_66 | F04-CHIKKANAHALLI | NAGASAMUDRA_66F04-CHIKKANAHALLI | 1310403902010100 | AGRI | 11.16 | 6.84 | 18 | 122 | 1 | 405 | 580.265 | 565.363 | 565.363 | 0 | 14.902 | 20000 | 298040 | 1 | 298040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298040 |  |  | 0 | 0 | 269725.108 | 0 | 269725.108 | 28314.892 | 9.5004 | 9.5 | 0.00036639 | 5-10 | 90.4996 | 90.4996 | 10121803 | 1569979.491 | 1569944.491 | 10121840.59 | 99.9978 | 9.5024 | 9.5024 | 5-10 | 99.9978 | 9.5024 | 5-10 |  | 269725.108 | 9.5004 | 5-10
24 | Non_RAPDRP | MOLAKALMURU | Nagasamudra | NAGASAMUDRA_66 | F05-BHATRAHALLI | NAGASAMUDRA_66F05-BHATRAHALLI | 1310403902010100 | NJY | 23.6056 | 14.44 | 38.0456 | 82 | 2250 | 0 | 2426.589 | 2397.096 | 2397.096 | 0 | 29.493 | 10000 | 294930 | 1 | 294930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294930 | 294930 | 0 | 0 | 0 | 243700.65 | 0 | 243700.65 | 51229.35 | 17.37 | 15.51 | 1.86 | 15-20 | 82.63 | 82.63 | 39191443 | 2481897.94 | 1535534.94 | 40137806 | 61.8694 | 48.8773 | 48.8773 | >30 | 61.8694 | 48.8773 | >30 |  | 243700.65 | 17.37 | 15-20 |  | 1)Due to line trouble load shifted on F06 Byrapura IP feeder
25 | Non_RAPDRP | MOLAKALMURU | Nagasamudra | NAGASAMUDRA_66 | F06-BYRAPURA | NAGASAMUDRA_66F06-BYRAPURA | 1310403902020300 | AGRI | 11.2 | 9.2 | 20.4 | 79 | 0 | 304 | 3271.2 | 3119.4 | 3119.4 | 0 | 151.8 | 2000 | 303600 | 1 | 303600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303600 |  |  | 0 | 0 | 274757.506 | 0 | 274757.506 | 28842.494 | 9.5002 | 9.5 | 0.00016271 | 5-10 | 90.4998 | 90.4998 | 7769784 | 1599088.297 | 1599088.619 | 7769784.05 | 100 | 9.5001 | 9.5001 | 5-10 | 100 | 9.5002 | 5-10 |  | 274757.506 | 9.5002 | 5-10
26 | Non_RAPDRP | MOLAKALMURU | Nagasamudra | NAGASAMUDRA_66 | F07-NAGASAMUDRA | NAGASAMUDRA_66F07-NAGASAMUDRA | 1310403902020300 | NJY | 12 | 9 | 21 | 25 | 1318 | 0 | 1853.5 | 1777.4 | 1777.4 | 0 | 76.1 | 2000 | 152200 | 1 | 152200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152200 | 152200 | 0 | 0 | 0 | 128251.5 | 0 | 128251.5 | 23948.5 | 15.7349 | 12.87 | 2.8649 | 15-20 | 84.2651 | 84.2651 | 17902379 | 1230792.78 | 623045.78 | 18510126 | 50.6215 | 57.3437 | 57.3437 | >30 | 50.6215 | 57.3437 | >30 |  | 128251.5 | 15.7349 | 15-20 | Assessed Energy | 01.Unauthourised IP sets 02.Most of the ipset has more load capacity than sanctioned load in the field
27 | Non_RAPDRP | MOLAKALMURU | Nagasamudra | NAGASAMUDRA_66 | F08-ROPPA | NAGASAMUDRA_66F08-ROPPA | 1310403902020300 | NJY | 23.07 | 18 | 41.07 | 74 | 2047 | 0 | 2639.7 | 2519.6 | 2519.6 | 0 | 120.1 | 2000 | 240200 | 1 | 240200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240200 | 240200 | 0 | 0 | 0 | 216981 | 0 | 216981 | 23219 | 9.6665 | 13.79 | -4.1235 | 5-10 | 90.3335 | 90.3335 | 40084406 | 2151997.13 | 1066036.13 | 41170367 | 49.5371 | 55.2515 | 55.2515 | >30 | 49.5371 | 55.2515 | >30 |  | 216981 | 9.6665 | 5-10
28 | Non_RAPDRP | MOLAKALMURU | Nagasamudra | NAGASAMUDRA_66 | F09-ASHOKA SIDDAPURA | NAGASAMUDRA_66F09-ASHOKA SIDDAPURA | 1310403902021500 | AGRI | 16.02 | 9.31 | 25.33 | 114 | 0 | 528 | 55.667 | 32.908 | 32.908 | 0 | 22.759 | 20000 | 455180 | 1 | 455180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455180 |  |  | 0 | 0 | 411938.274 | 0 | 411938.274 | 43241.726 | 9.4999 | 9.5 | -8.2165e-05 | 5-10 | 90.5001 | 90.5001 | 9468916 | 2397480.602 | 2397480.602 | 9468916 | 100 | 9.4999 | 9.4999 | 5-10 | 100 | 9.4999 | 5-10 |  | 411938.274 | 9.4999 | 5-10
29 | Non_RAPDRP | MOLAKALMURU | Rampura | RAMPURA_66 | F01-DEVASAMUDRA | RAMPURA_66F01-DEVASAMUDRA | 1310403903010100 | AGRI | 20.296 | 12.16 | 32.456 | 126 | 1 | 587 | 785.682 | 769.632 | 769.632 | 0 | 16.05 | 20000 | 321000 | 1 | 321000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321000 |  |  | 0 | 0 | 290503.191 | 0 | 290503.191 | 30496.809 | 9.5006 | 9.5 | 0.00056355 | 5-10 | 90.4994 | 90.4994 | 12956896 | 1690907.781 | 1690907.781 | 12956896 | 100 | 9.5006 | 9.5006 | 5-10 | 100 | 9.5006 | 5-10 |  | 290503.191 | 9.5006 | 5-10
30 | Non_RAPDRP | MOLAKALMURU | Rampura | RAMPURA_66 | F02-JBHALLI | RAMPURA_66F02-JBHALLI | 1310403903010100 | AGRI | 15.525 | 9.5 | 25.025 | 121 | 0 | 274 | 816.819 | 790.726 | 790.726 | 0 | 26.093 | 20000 | 521860 | 1 | 521860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521860 |  |  | 0 | 0 | 401500 | 0 | 401500 | 120360 | 23.0637 | 23.06 | 0.0036569 | 20-30 | 76.9363 | 76.9363 | 6355210 | 2336730 | 2336730 | 6355211.29 | 100 | 23.0637 | 23.0637 | 20-30 | 100 | 23.0637 | 20-30 |  | 401500 | 23.0637 | 20-30 | Assessed Energy | 01.Unauthourised IP sets 02.Most of the ipset has more load capacity than sanctioned load in the field
31 | Non_RAPDRP | MOLAKALMURU | Rampura | RAMPURA_66 | F04-NJY SRJ | RAMPURA_66F04-NJY SRJ | 1310403903010100 | NJY | 11.78 | 7.22 | 19 | 30 | 1757 | 0 | 847.551 | 824.827 | 824.827 | 0 | 22.724 | 10000 | 227240 | 1 | 227240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227240 |  |  | 0 | 0 | 219785.5 | 0 | 219785.5 | 7454.5 | 3.2805 | 3.28 | 0.00045239 | 0-5 | 96.7195 | 96.7195 | 44210346 | 2037437.25 | 957923.84 | 45289859.41 | 47.0161 | 54.5262 | 54.5262 | >30 | 47.0161 | 54.5262 | >30 |  | 219785.5 | 3.2805 | 0-5
32 | Non_RAPDRP | MOLAKALMURU | Rampura | RAMPURA_66 | F05-RAMPURA | RAMPURA_66F05-RAMPURA | 1310403903020300 | AGRI | 13.02 | 7.98 | 21 | 55 | 3 | 584 | 479.464 | 470.945 | 470.945 | 0 | 8.519 | 20000 | 170380 | 1 | 170380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170380 |  |  | 0 | 0 | 154192.075 | 0 | 154192.075 | 16187.925 | 9.5011 | 9.5 | 0.0010711 | 5-10 | 90.4989 | 90.4989 | 13369802 | 897817.821 | 897799.821 | 13369820 | 99.998 | 9.5029 | 9.5029 | 5-10 | 99.998 | 9.5029 | 5-10 |  | 154192.075 | 9.5011 | 5-10
33 | Non_RAPDRP | MOLAKALMURU | Rampura | RAMPURA_66 | F06-NRK PURA | RAMPURA_66F06-NRK PURA | 1310403903020300 | AGRI | 14.847 | 7.98 | 22.827 | 78 | 0 | 478 | 718.899 | 698.812 | 698.812 | 0 | 20.087 | 20000 | 401740 | 1 | 401740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401740 |  |  | 0 | 0 | 418249.65 | 0 | 418249.65 | -16509.65 | -4.1095 | -4.11 | 0.00046398 | <0 | 104.1095 | 104.1095 | 8771604 | 2434213.001 | 2434213.001 | 8771604 |  | 100 | 100 | >30 | 100 | -4.1095 | <0 |  | 418249.65 | -4.1095 | <0 | Import | 1)Due to line trouble load shifted on F03 MURUDI
34 | Non_RAPDRP | MOLAKALMURU | Rampura | RAMPURA_66 | F07-BANDRAVI | RAMPURA_66F07-BANDRAVI | 1310403903020300 | MIXED LOAD | 22.42 | 13.68 | 36.1 | 199 | 1051 | 457 | 1393.527 | 1357.997 | 1357.997 | 0 | 35.53 | 20000 | 710600 | 1 | 710600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710600 |  |  | 0 | 0 | 525938.863 | 0 | 525938.863 | 184661.137 | 25.9867 | 25.99 | -0.0033497 | 20-30 | 74.0133 | 74.0133 | 18330748 | 3449784.303 | 3102656.303 | 18677877.21 | 89.9377 | 33.4341 | 33.4341 | >30 | 89.9377 | 33.4341 | >30 | 0 | 525938.863 | 25.9867 | 20-30 | Assessed Energy | 1)Dnauthorised IP sets 2)Feeder length more than 48KM 3)Feeder have 2/4 ACSR conductor 4)Most of the ipset has more load capacity than sanctioned load in the field.3) In idea software per hp consumption of agri feeder is accounted less than actual avg sub division agri consumption
35 | Non_RAPDRP | MOLAKALMURU | Rampura | RAMPURA_66 | F08-THAMMENAHALLI | RAMPURA_66F08-THAMMENAHALLI | 1310403903020300 | AGRI | 19.43 | 10.64 | 30.07 | 186 | 3 | 424 | 1147.226 | 1113.676 | 1113.676 | 0 | 33.55 | 20000 | 671000 | 1 | 671000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 671000 |  |  | 0 | 0 | 613520 | 0 | 613520 | 57480 | 8.5663 | 8.57 | -0.0036811 | 5-10 | 91.4337 | 91.4337 | 10637087 | 3573274.19 | 3570964.19 | 10639398.63 | 99.9354 | 8.6254 | 8.6254 | 5-10 | 99.9354 | 8.6254 | 5-10 |  | 613520 | 8.5663 | 5-10
36 | Non_RAPDRP | MOLAKALMURU | Rampura | RAMPURA_66 | F09-RAMASAGARINDUSTRIAL | RAMPURA_66F09-RAMASAGARINDUSTRIAL | 1310403903010100 | INDUSTRIAL | 12 | 0 | 12 | 4 | 1 | 0 | 1514.935 | 1498.208 | 1498.208 | 0 | 16.727 | 10000 | 167270 | 1 | 167270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167270 |  |  | 0 | 0 | 156790 | 0 | 156790 | 10480 | 6.2653 | 6.27 | -0.0046805 | 5-10 | 93.7347 | 93.7347 | 0 | 1350222 | 1350222 | 0 | 100 | 6.2653 | 6.2653 | 5-10 | 100 | 6.2653 | 5-10 |  | 156790 | 6.2653 | 5-10
37 | Non_RAPDRP | MOLAKALMURU | Rampura | RAMPURA_66 | F10-TOWN NJY | RAMPURA_66F10-TOWN NJY | 1310403903010200 | NJY | 11.16 | 6.84 | 18 | 76 | 4443 | 0 | 2535.394 | 2486.341 | 2486.341 | 0 | 49.053 | 10000 | 490530 | 1 | 490530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490530 |  |  | 0 | 0 | 426623 | 0 | 426623 | 63907 | 13.0282 | 13.03 | -0.0018468 | 10-15 | 86.9718 | 86.9718 | 38716599.92 | 4125488.75 | 2511807.16 | 40330281.51 | 60.8851 | 47.0471 | 47.0471 | >30 | 60.8851 | 47.0471 | >30 |  | 426623 | 13.0282 | 10-15
38 | Non_RAPDRP | MOLAKALMURU | Rampura | RAMPURA_66 | F11- NJY HANUMANAGUDDA | RAMPURA_66F11- NJY HANUMANAGUDDA | 1310403903020300 | NJY | 12.4 | 7.6 | 20 | 30 | 1821 | 0 | 4483.7 | 4248.7 | 4248.7 | 0 | 235 | 1000 | 235000 | 1 | 235000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235000 |  |  | 0 | 0 | 219534 | 0 | 219534 | 15466 | 6.5813 | 6.58 | 0.0012766 | 5-10 | 93.4187 | 93.4187 | 49585005 | 2105362.86 | 990781.44 | 50699586.42 | 47.0599 | 56.0373 | 56.0373 | >30 | 47.0599 | 56.0373 | >30 |  | 219534 | 6.5813 | 5-10
39 | Non_RAPDRP | MOLAKALMURU | Rampura | RAMPURA_66 | F12-NJY BOMMADEVARAHALLY | RAMPURA_66F12-NJY BOMMADEVARAHALLY | 1310403903020300 | NJY | 11.78 | 7.22 | 19 | 80 | 2205 | 0 | 1719.328 | 1678.241 | 1678.241 | 0 | 41.087 | 10000 | 410870 | 1 | 410870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410870 |  |  | 0 | 0 | 370025.65 | 1 | 370026.65 | 40843.35 | 9.9407 | 9.94 | 0.000699 | 5-10 | 90.0593 | 90.0593 | 46216811 | 3595132.67 | 1470046.73 | 48341896.94 | 40.8899 | 63.1748 | 63.1748 | >30 | 40.8899 | 63.1748 | >30 |  | 370026.65 | 9.9407 | 5-10
40 | Non_RAPDRP | MOLAKALMURU | Rampura | RAMPURA_66 | F03-MURUDI | RAMPURA_66F03-MURUDI | 1310403903020300 | AGRI | 17.14 | 10.26 | 27.4 | 173 | 0 | 231 | 881.541 | 852.907 | 852.907 | 0 | 28.634 | 20000 | 572680 | 1 | 572680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572680 |  |  | 0 | 0 | 335200 | 0 | 335200 | 237480 | 41.4682 | 41.47 | -0.0018153 | >30 | 58.5318 | 58.5318 | 5391609 | 1950864 | 1950864 | 5391609 | 100 | 41.4682 | 41.4682 | >30 | 100 | 41.4682 | >30 |  | 335200 | 41.4682 | >30 | Export/assessed sales | 1)Due to line trouble(F06 NRK PURA) load shifted on F03 MURUDI 2)Unauthorised IP sets
41 | Non_RAPDRP | MOLAKALMURU | B.G.kere | KONASAGARA_66 | F01-BELAVINAMARADAHATTY | KONASAGARA_66F01-BELAVINAMARADAHATTY | 1310403905010100 | AGRI | 16.85 | 12.6 | 29.45 | 163 | 0 | 229 | 2673.8 | 2555.1 | 2555.1 | 0 | 118.7 | 2000 | 237400 | 1 | 237400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237400 |  |  | 0 | 0 | 173582.334 | 0 | 173582.334 | 63817.666 | 26.8819 | 26.88 | 0.0019149 | 20-30 | 73.1181 | 73.1181 | 5500551 | 1018928.97 | 1018928.226 | 5500551.07 | 99.9999 | 26.882 | 26.882 | 20-30 | 99.9999 | 26.882 | 20-30 |  | 173582.334 | 26.8819 | 20-30 | Assessed Energy | 01.Unauthourised IP sets 02.Most of the ipset has more load capacity than sanctioned load in the field
42 | NON RAPDRP | MOLAKALMURU | B.G.kere | KONASAGARA_66 | F02-NETHRANAHALLY | KONASAGARA_66F02-NETHRANAHALLY | 1310403905010100 | AGRI | 11.78 | 7.22 | 19 | 87 | 3 | 328 | 3747.6 | 3605.2 | #N/A | #N/A | 142.4 | 2000 | 284800 | 1 | 284800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284800 |  |  | 0 | 0 | 257744.963 | 0 | 257744.963 | 27055.037 | 9.4997 | 9.5 | -0.00033813 | 5-10 | 90.5003 | 90.5003 | 2730035 | 1500581.37 | 1500676.658 | 2729940.15 | 100.0064 | 9.4939 | 9.4939 | 5-10 | 100 | 9.4997 | 5-10 |  | 257744.963 | 9.4997 | 5-10
43 | NON RAPDRP | MOLAKALMURU | B.G.kere | KONASAGARA_66 | F03-MARAMMANAHALLY | KONASAGARA_66F03-MARAMMANAHALLY | 1310403905010100 | AGRI | 12.6 | 8.6 | 21.2 | 0 | 1 | 145 | 1641.6 | 1572.5 | #N/A | #N/A | 69.1 | 2000 | 138200 | 1 | 138200 | 0 | 0 | 0 | 0 | 18000 | 18000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156200 |  |  | 0 | 0 | 146768.09 | 0 | 146768.09 | 9431.91 | 6.0384 | 6.04 | -0.0016453 | 5-10 | 93.9616 | 93.9616 | 2800809 | 862293.9 | 861094.229 | 2802008.82 | 99.8609 | 6.1691 | 6.1691 | 5-10 | 99.8609 | 6.1691 | 5-10 |  | 146768.09 | 6.0384 | 5-10
44 | NON RAPDRP | MOLAKALMURU | B.G.kere | KONASAGARA_66 | F04-KONASAGARA NJY | KONASAGARA_66F04-KONASAGARA NJY | 1310403905010100 | NJY | 8.68 | 5.32 | 14 | 76 | 2056 | 0 | 3754.2 | 3652.3 | #N/A | #N/A | 101.9 | 2000 | 203800 | 1 | 203800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203800 |  |  | 0 | 0 | 189820 | 0 | 189820 | 13980 | 6.8597 | 6.86 | -0.00033366 | 5-10 | 93.1403 | 93.1403 | 25367859 | 1833315.99 | 987097.43 | 26214077.56 | 53.8422 | 49.8512 | 49.8512 | >30 | 53.8422 | 49.8512 | >30 |  | 189820 | 6.8597 | 5-10
45 | NON RAPDRP | MOLAKALMURU | B.G.kere | KONASAGARA_66 | F05-CHOWDIPURA | KONASAGARA_66F05-CHOWDIPURA | 1310403905010100 | AGRI | 11.16 | 6.84 | 18 | 65 | 0 | 157 | 3328.4 | 3190.5 | #N/A | #N/A | 137.9 | 2000 | 275800 | 1 | 275800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275800 |  |  | 0 | 0 | 177000 | 0 | 177000 | 98800 | 35.8231 | 35.82 | 0.0030602 | >30 | 64.1769 | 64.1769 | 2416497 | 1030140 | 1030140 | 2416497 | 100 | 35.8231 | 35.8231 | >30 | 100 | 35.8231 | >30 |  | 177000 | 35.8231 | >30 | Assessed Energy | 01.Unauthourised IP sets 02.Most of the ipset has more load capacity than sanctioned load in the field
46 | NON RAPDRP | MOLAKALMURU | B.G.kere | KONASAGARA_66 | F06-UDEVU | KONASAGARA_66F06-UDEVU | 1310403905010100 | AGRI | 11.302 | 6.46 | 17.762 | 28 | 0 | 219 | 4674.3 | 4462.6 | #N/A | #N/A | 211.7 | 2000 | 423400 | 1 | 423400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 15000 | 0 | 0 | 0 | 408400 |  |  | 0 | 0 | 234200 | 0 | 234200 | 174200 | 42.6543 | 42.65 | 0.0042605 | >30 | 57.3457 | 57.3457 | 7354518 | 1363044 | 1363044 | 7354518 | 100 | 42.6543 | 42.6543 | >30 | 100 | 42.6543 | >30 | 0 | 234200 | 42.6543 | >30 | Assessed Energy | 01.Unauthourised IP sets 02.Most of the ipset has more load capacity than sanctioned load in the field
1 | NON RAPDRP | THALLAK | HIREHALLI | GOWRASAMUDRA_66 | F01-MARAMMADEVI | GOWRASAMUDRA_66F01-MARAMMADEVI | 1310403901010101 | AGRI | 9.8 | 9.1 | 18.9 | 103 | 1 | 508 | 596.68 | 567.98 | 567.98 | 0 | 28.7 | 20000 | 574000 | 0.8694 | 574000 | 0 | 0 | 0 | 0 | 45000 | 45000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619000 |  |  | 0 | 0 | 1 | 560193.316 | 560194.316 | 58805.684 | 9.5001 | 9.5 | 0.0001105 | 5-10 | 90.4999 | 90.4999 | 11295380 | 3260457.026 | 3260325.026 | 11295512.77 | 99.996 | 9.5038 | 9.5038 | 5-10 | 99.996 | 9.5038 | 5-10 |  | 560194.316 | 9.5001 | 5-10
2 | NON RAPDRP | THALLAK | HIREHALLI | GOWRASAMUDRA_66 | F02-MITLAKATTE | GOWRASAMUDRA_66F02-MITLAKATTE | 1310403901020101 | AGRI | 14.6 | 4.73 | 19.33 | 99 | 8 | 186 | 491.223 | 469.97 | 469.97 | 0 | 21.253 | 20000 | 425060 | 0.8694 | 425060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58000 | 58000 | 0 | 0 | 0 | 367060 |  |  | 0 | 0 | 259 | 217100 | 217359 | 149701 | 40.7838 | 40.78 | 0.0037956 | >30 | 59.2162 | 85.2604 | 2588313 | 1266590.91 | 1266509.91 | 2588394.25 | 99.9936 | 40.7876 | 14.745 | >30 | 99.9936 | 14.745 | 10-15 | 95598 | 312957 | 14.7396 | 10-15 | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 186 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 186 * 5 HP = 930 HP - 186 * 8 HP = 1488 HP ) = 558 HP 394.68817204301 Units per HP consumption taken for calculation Assesed cosumpion of 95598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 186 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 186 * 5 HP = 930 HP - 186 * 8 HP = 1488 HP ) = 558 HP 394.68817204301 Units per HP consumption taken for calculation Assesed cosumpion of 95598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 186 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 186 * 5 HP = 930 HP - 186 * 8 HP = 1488 HP ) = 558 HP 394.68817204301 Units per HP consumption taken for calculation Assesed cosumpion of 95598 units will bring down the T&D less then the 10% | *Proposed to byfergate the IP load to the respective IP feeder *Proposed reconductpring of HT and LT lines in the Feeder *Proposed to byfurcate the IP set from the Domestic feeder to agri feeder in RDSS *proposed vigilence activity in the Judistriction *proposed to replace the Electromechanical to Electrostatic in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 186 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 186 * 5 HP = 930 HP - 186 * 8 HP = 1488 HP ) = 558 HP 394.68817204301 Units per HP consumption taken for calculation Assesed cosumpion of 95598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 186 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 186 * 5 HP = 930 HP - 186 * 8 HP = 1488 HP ) = 558 HP 394.68817204301 Units per HP consumption taken for calculation Assesed cosumpion of 95598 units will bring down the T&D less then the 10%
3 | NON RAPDRP | THALLAK | HIREHALLI | GOWRASAMUDRA_66 | F03-MALLASAMUDRA | GOWRASAMUDRA_66F03-MALLASAMUDRA | 1310403901020102 | AGRI | 13.65 | 22.35 | 36 | 94 | 0 | 162 | 448.495 | 426.75 | 426.75 | 0 | 21.745 | 20000 | 434900 | 0.8694 | 434900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434900 |  |  | 0 | 0 | 0 | 182300 | 182300 | 252600 | 58.0823 | 58.08 | 0.0023178 | >30 | 41.9177 | 85.5135 | 3082266 | 1060986 | 1060986 | 3082266.21 | 100 | 58.0823 | 14.4865 | >30 | 100 | 14.4865 | 10-15 | 189598 | 371898 | 14.4865 | 10-15 | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 162 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 162 * 5 HP = 810 HP - 162 * 8 HP = 1296 HP ) = 486 HP 536.913580246914 Units per HP consumption taken for calculation Assesed cosumpion of 189598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 162 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 162 * 5 HP = 810 HP - 162 * 8 HP = 1296 HP ) = 486 HP 536.913580246914 Units per HP consumption taken for calculation Assesed cosumpion of 189598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 162 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 162 * 5 HP = 810 HP - 162 * 8 HP = 1296 HP ) = 486 HP 536.913580246914 Units per HP consumption taken for calculation Assesed cosumpion of 189598 units will bring down the T&D less then the 10% | *Proposed to byfergate the IP load to the respective IP feeder *Proposed reconductpring of HT and LT lines in the Feeder *Proposed to byfurcate the IP set from the Domestic feeder to agri feeder in RDSS *proposed vigilence activity in the Judistriction *proposed to replace the Electromechanical to Electrostatic in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 162 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 162 * 5 HP = 810 HP - 162 * 8 HP = 1296 HP ) = 486 HP 536.913580246914 Units per HP consumption taken for calculation Assesed cosumpion of 189598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 162 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 162 * 5 HP = 810 HP - 162 * 8 HP = 1296 HP ) = 486 HP 536.913580246914 Units per HP consumption taken for calculation Assesed cosumpion of 189598 units will bring down the T&D less then the 10%
4 | NON RAPDRP | THALLAK | THALLAK | GOWRASAMUDRA_66 | F04-BUKKAMBUDI | GOWRASAMUDRA_66F04-BUKKAMBUDI | 1310403901020103 | AGRI | 17.65 | 20.4825 | 38.1325 | 48 | 4 | 545 | 604.715 | 578.16 | 578.16 | 0 | 26.555 | 20000 | 531100 | 0.8694 | 531100 | 0 | 0 | 0 | 0 | 135000 | 135000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 666100 |  |  | 0 | 0 | 260 | 602561.491 | 602821.491 | 63278.509 | 9.4999 | 9.5 | -0.00014878 | 5-10 | 90.5001 | 90.5001 | 13924436 | 3509200.417 | 3509010.417 | 13924626.96 | 99.9946 | 9.5048 | 9.5048 | 5-10 | 99.9946 | 9.5048 | 5-10 |  | 602821.491 | 9.4999 | 5-10
5 | NON RAPDRP | THALLAK | THALLAK | GOWRASAMUDRA_66 | F05-KAKIBORANAHATTI | GOWRASAMUDRA_66F05-KAKIBORANAHATTI | 1310403901010103 | AGRI | 10 | 12 | 22 | 39 | 179 | 87 | 356.58 | 331.77 | 331.77 | 0 | 24.81 | 20000 | 496200 | 0.464 | 496200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275000 | 275000 | 0 | 0 | 0 | 221200 |  |  | 0 | 0 | 7869 | 94700 | 102569 | 118631 | 53.6307 | 53.63 | 0.00065099 | >30 | 46.3693 | 85.5185 | 3035951 | 638689.44 | 623248.44 | 3051392.03 | 97.5824 | 54.7517 | 16.549 | >30 | 97.5824 | 16.549 | 15-20 | 86598 | 189167 | 14.4815 | 10-15 | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 87 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 87 * 5 HP = 435 HP - 87 * 8 HP = 696 HP ) = 261 HP 508.505747126437 Units per HP consumption taken for calculation Assesed cosumpion of 86598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 87 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 87 * 5 HP = 435 HP - 87 * 8 HP = 696 HP ) = 261 HP 508.505747126437 Units per HP consumption taken for calculation Assesed cosumpion of 86598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 87 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 87 * 5 HP = 435 HP - 87 * 8 HP = 696 HP ) = 261 HP 508.505747126437 Units per HP consumption taken for calculation Assesed cosumpion of 86598 units will bring down the T&D less then the 10% | *Proposed to byfergate the IP load to the respective IP feeder *Proposed reconductpring of HT and LT lines in the Feeder *Proposed to byfurcate the IP set from the Domestic feeder to agri feeder in RDSS *proposed vigilence activity in the Judistriction *proposed to replace the Electromechanical to Electrostatic in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 87 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 87 * 5 HP = 435 HP - 87 * 8 HP = 696 HP ) = 261 HP 508.505747126437 Units per HP consumption taken for calculation Assesed cosumpion of 86598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 87 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 87 * 5 HP = 435 HP - 87 * 8 HP = 696 HP ) = 261 HP 508.505747126437 Units per HP consumption taken for calculation Assesed cosumpion of 86598 units will bring down the T&D less then the 10%
6 | NON RAPDRP | THALLAK | HIREHALLI | GOWRASAMUDRA_66 | F07-HANUMANTHANAHALLI | GOWRASAMUDRA_66F07-HANUMANTHANAHALLI | 1310403901010301 | AGRI | 12 | 10 | 22 | 60 | 4 | 173 | 381.517 | 362.96 | 362.96 | 0 | 18.557 | 20000 | 371140 | 0.464 | 371140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148300 | 148300 | 0 | 0 | 0 | 222840 |  |  | 0 | 0 | 183 | 201486.73 | 201669.73 | 21170.27 | 9.5002 | 9.5 | 0.00021091 | 5-10 | 90.4998 | 90.4998 | 3851451 | 1174684.218 | 1174175.218 | 3851960.26 | 99.9567 | 9.5394 | 9.5394 | 5-10 | 99.9567 | 9.5394 | 5-10 |  | 201669.73 | 9.5002 | 5-10
7 | NON RAPDRP | THALLAK | HIREHALLI | GOWRASAMUDRA_66 | F08-ANJANEYA SWAMY NJY | GOWRASAMUDRA_66F08-ANJANEYA SWAMY NJY | 1310403901010302 | NJY | 7.65 | 8.95 | 16.6 | 22 | 747 | 0 | 255.389 | 249.18 | 249.18 | 0 | 6.209 | 20000 | 124180 | 0.464 | 124180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32000 | 32000 | 0 | 0 | 0 | 92180 |  |  | 0 | 0 | 78877 | 0 | 78877 | 13303 | 14.4315 | 14.43 | 0.001547 | 10-15 | 85.5685 | 85.5685 | 18747910 | 778532.19 | 282993.19 | 19243449 | 36.3496 | 68.8962 | 68.8962 | >30 | 36.3496 | 68.8962 | >30 |  | 78877 | 14.4315 | 10-15
8 | NON RAPDRP | THALLAK | THALLAK | GOWRASAMUDRA_66 | F11-NJY HONNURU | GOWRASAMUDRA_66F11-NJY HONNURU | 1310403901010102 | NJY | 18.65 | 16.78 | 35.43 | 22 | 1431 | 0 | 7492 | 7351.1 | 7351.1 | 0 | 140.9 | 1000 | 140900 | 0.8694 | 140900 | 0 | 0 | 0 | 0 | 24390 | 24390 | 0 | 0 | 0 | 0 | 9000 | 9000 | 0 | 0 | 0 | 156290 |  |  | 0 | 0 | 135146 | 0 | 135146 | 21144 | 13.5287 | 13.53 | -0.0013033 | 10-15 | 86.4713 | 86.4713 | 18020886 | 1317423.2 | 696065.76 | 18642243.44 | 52.8354 | 54.3125 | 54.3125 | >30 | 52.8354 | 54.3125 | >30 |  | 135146 | 13.5287 | 10-15
9 | NON RAPDRP | THALLAK | HIREHALLI | GOWRASAMUDRA_66 | F6-NJY BANDETHIMMALAPURA | GOWRASAMUDRA_66F6-NJY BANDETHIMMALAPURA | 1310403901020104 | NJY | 18.23 | 13.2 | 31.43 | 24 | 1291 | 0 | 489.78 | 476.58 | 476.58 | 0 | 13.2 | 10000 | 132000 | 0.464 | 132000 | 0 | 0 | 0 | 0 | 9000 | 9000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141000 |  |  | 0 | 0 | 128061.4 | 0 | 128061.4 | 12938.6 | 9.1763 | 9.18 | -0.0036879 | 5-10 | 90.8237 | 90.8237 | 17865498 | 1213612.67 | 553491.67 | 18525619 | 45.6069 | 58.5781 | 58.5781 | >30 | 45.6069 | 58.5781 | >30 |  | 128061.4 | 9.1763 | 5-10
10 | NON RAPDRP | THALLAK | DODDAULLARTHI | MYLANAHALLI_66 | F01-OBALAPURA | MYLANAHALLI_66F01-OBALAPURA | 1310402901010101 | AGRI | 18.6 | 23.195 | 41.795 | 117 | 23 | 423 | 1135.38 | 1135.38 | 1135.38 | 0 | 0 | 20000 | 0 | 0.82907 | 0 | 0 | 0 | 0 | 0 | 540600 | 540600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540600 |  |  | 0 | 0 | 498 | 459200 | 459698 | 80902 | 14.9652 | 14.97 | -0.0047762 | 10-15 | 85.0348 | 85.0348 | 2951005 | 2679212.52 | 2679127.52 | 2951090.36 | 99.9968 | 14.9679 | 14.9679 | 10-15 | 99.9968 | 14.9679 | 10-15 |  | 459698 | 14.9652 | 10-15
11 | NON RAPDRP | THALLAK | THALLAK | MYLANAHALLI_66 | F02-BHOGANAHALLI | MYLANAHALLI_66F02-BHOGANAHALLI | 1310402901010102 | AGRI | 17.85 | 22.48 | 40.33 | 76 | 0 | 337 | 69.349 | 45.11 | 45.11 | 0 | 24.239 | 20000 | 484780 | 0.82907 | 484780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 484780 |  |  | 0 | 0 | 0 | 369800 | 369800 | 114980 | 23.718 | 23.72 | -0.0020248 | 20-30 | 76.282 | 85.0691 | 6268117.97 | 2152236 | 2152236 | 6268117.64 | 100 | 23.718 | 14.9309 | 20-30 | 100 | 14.9309 | 10-15 | 42598 | 412398 | 14.9309 | 10-15 | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 337 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 337 * 5 HP = 1685 HP - 337 * 8 HP = 2696 HP ) = 1011 HP 287.703264094956 Units per HP consumption taken for calculation Assesed cosumpion of 42598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 337 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 337 * 5 HP = 1685 HP - 337 * 8 HP = 2696 HP ) = 1011 HP 287.703264094956 Units per HP consumption taken for calculation Assesed cosumpion of 42598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 337 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 337 * 5 HP = 1685 HP - 337 * 8 HP = 2696 HP ) = 1011 HP 287.703264094956 Units per HP consumption taken for calculation Assesed cosumpion of 42598 units will bring down the T&D less then the 10% | *Proposed to byfergate the IP load to the respective IP feeder *Proposed reconductpring of HT and LT lines in the Feeder *Proposed to byfurcate the IP set from the Domestic feeder to agri feeder in RDSS *proposed vigilence activity in the Judistriction *proposed to replace the Electromechanical to Electrostatic in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 337 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 337 * 5 HP = 1685 HP - 337 * 8 HP = 2696 HP ) = 1011 HP 287.703264094956 Units per HP consumption taken for calculation Assesed cosumpion of 42598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 337 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 337 * 5 HP = 1685 HP - 337 * 8 HP = 2696 HP ) = 1011 HP 287.703264094956 Units per HP consumption taken for calculation Assesed cosumpion of 42598 units will bring down the T&D less then the 10%
12 | NON RAPDRP | THALLAK | THALLAK | MYLANAHALLI_66 | F03-CNHALLI | MYLANAHALLI_66F03-CNHALLI | 1310402901010103 | AGRI | 18.95 | 18.38 | 37.33 | 64 | 0 | 416 | 763.46 | 763.46 | 763.46 | 0 | 0 | 20000 | 0 | 0.82907 | 0 | 0 | 0 | 0 | 0 | 530360 | 530360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530360 |  |  | 0 | 0 | 0 | 459900 | 459900 | 70460 | 13.2853 | 13.29 | -0.0046844 | 10-15 | 86.7147 | 86.7147 | 9336916 | 2676618 | 2676718 | 9336815.45 | 100.0037 | 13.2821 | 13.2821 | 10-15 | 100 | 13.2853 | 10-15 |  | 459900 | 13.2853 | 10-15
13 | NON RAPDRP | THALLAK | DODDAULLARTHI | MYLANAHALLI_66 | F04-BASAPURA | MYLANAHALLI_66F04-BASAPURA | 1310402901010104 | AGRI | 21.65 | 16.38 | 38.03 | 89 | 2 | 378 | 789.418 | 752.73 | 752.73 | 0 | 36.688 | 20000 | 733760 | 0.82907 | 733760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190000 | 190000 | 0 | 0 | 0 | 543760 |  |  | 0 | 0 | 19 | 409000 | 409019 | 134741 | 24.7795 | 24.78 | -0.00050169 | 20-30 | 75.2205 | 85.0774 | 2021029 | 2380749.08 | 2380890.08 | 2020887.6 | 100.0059 | 24.775 | 14.9175 | 20-30 | 100 | 14.9226 | 10-15 | 53598 | 462617 | 14.9226 | 10-15 | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 378 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 378 * 5 HP = 1890 HP - 378 * 8 HP = 3024 HP ) = 1134 HP 287.703703703704 Units per HP consumption taken for calculation Assesed cosumpion of 53598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 378 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 378 * 5 HP = 1890 HP - 378 * 8 HP = 3024 HP ) = 1134 HP 287.703703703704 Units per HP consumption taken for calculation Assesed cosumpion of 53598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 378 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 378 * 5 HP = 1890 HP - 378 * 8 HP = 3024 HP ) = 1134 HP 287.703703703704 Units per HP consumption taken for calculation Assesed cosumpion of 53598 units will bring down the T&D less then the 10% | *Proposed to byfergate the IP load to the respective IP feeder *Proposed reconductpring of HT and LT lines in the Feeder *Proposed to byfurcate the IP set from the Domestic feeder to agri feeder in RDSS *proposed vigilence activity in the Judistriction *proposed to replace the Electromechanical to Electrostatic in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 378 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 378 * 5 HP = 1890 HP - 378 * 8 HP = 3024 HP ) = 1134 HP 287.703703703704 Units per HP consumption taken for calculation Assesed cosumpion of 53598 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 378 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 378 * 5 HP = 1890 HP - 378 * 8 HP = 3024 HP ) = 1134 HP 287.703703703704 Units per HP consumption taken for calculation Assesed cosumpion of 53598 units will bring down the T&D less then the 10%
14 | NON RAPDRP | THALLAK | THALLAK | MYLANAHALLI_66 | F05-MYLENAHALLI | MYLANAHALLI_66F05-MYLENAHALLI | 1310402901010105 | AGRI | 17.98 | 18.05 | 36.03 | 103 | 0 | 247 | 760.799 | 747.51 | 747.51 | 0 | 13.289 | 20000 | 265780 | 0.414 | 265780 | 0 | 0 | 0 | 0 | 30000 | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295780 |  |  | 0 | 0 | 0 | 267680.735 | 267680.735 | 28099.265 | 9.5001 | 9.5 | 5.5785e-05 | 5-10 | 90.4999 | 90.4999 | 5871849 | 1557901.766 | 1557901.827 | 5871850.51 | 100 | 9.5001 | 9.5001 | 5-10 | 100 | 9.5001 | 5-10 |  | 267680.735 | 9.5001 | 5-10
15 | NON RAPDRP | THALLAK | DODDAULLARTHI | MYLANAHALLI_66 | F06-DONNEHALLI | MYLANAHALLI_66F06-DONNEHALLI | 1310402901020301 | AGRI | 22.65 | 23.35 | 46 | 116 | 8 | 244 | 49.512 | 26.68 | 26.68 | 0 | 22.832 | 20000 | 456640 | 0.414 | 456640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 456640 |  |  | 0 | 0 | 3222 | 274500 | 277722 | 178918 | 39.1814 | 39.18 | 0.0014121 | >30 | 60.8186 | 85.3138 | 2666360.96 | 1636507.28 | 1598809.28 | 2704057.98 | 97.6964 | 40.5824 | 16.6514 | >30 | 97.6964 | 16.6514 | 15-20 | 111855 | 389577 | 14.6862 | 10-15 | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 244 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 244 * 5 HP = 1220 HP - 244 * 8 HP = 1952 HP ) = 732 HP 374.295081967213 Units per HP consumption taken for calculation Assesed cosumpion of 111855 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 244 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 244 * 5 HP = 1220 HP - 244 * 8 HP = 1952 HP ) = 732 HP 374.295081967213 Units per HP consumption taken for calculation Assesed cosumpion of 111855 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 244 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 244 * 5 HP = 1220 HP - 244 * 8 HP = 1952 HP ) = 732 HP 374.295081967213 Units per HP consumption taken for calculation Assesed cosumpion of 111855 units will bring down the T&D less then the 10% | *Proposed to byfergate the IP load to the respective IP feeder *Proposed reconductpring of HT and LT lines in the Feeder *Proposed to byfurcate the IP set from the Domestic feeder to agri feeder in RDSS *proposed vigilence activity in the Judistriction *proposed to replace the Electromechanical to Electrostatic in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 244 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 244 * 5 HP = 1220 HP - 244 * 8 HP = 1952 HP ) = 732 HP 374.295081967213 Units per HP consumption taken for calculation Assesed cosumpion of 111855 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 244 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 244 * 5 HP = 1220 HP - 244 * 8 HP = 1952 HP ) = 732 HP 374.295081967213 Units per HP consumption taken for calculation Assesed cosumpion of 111855 units will bring down the T&D less then the 10%
16 | NON RAPDRP | THALLAK | DODDAULLARTHI | MYLANAHALLI_66 | F07-THIPPAREDDYHALLI | MYLANAHALLI_66F07-THIPPAREDDYHALLI | 1310402901020302 | AGRI | 20.68 | 27.32 | 48 | 89 | 0 | 446 | 822.636 | 793.03 | 793.03 | 0 | 29.606 | 20000 | 592120 | 0.414 | 592120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592120 |  |  | 0 | 0 | 0 | 485400 | 485400 | 106720 | 18.0234 | 18.02 | 0.0033736 | 15-20 | 81.9766 | 85.1609 | 2128845.83 | 2825028 | 2825028 | 2128844.51 | 100 | 18.0234 | 14.8391 | 15-20 | 100 | 14.8391 | 10-15 | 18855 | 504255 | 14.8391 | 10-15 | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 446 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 446 * 5 HP = 2230 HP - 446 * 8 HP = 3568 HP ) = 1338 HP 265.52466367713 Units per HP consumption taken for calculation Assesed cosumpion of 18855 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 446 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 446 * 5 HP = 2230 HP - 446 * 8 HP = 3568 HP ) = 1338 HP 265.52466367713 Units per HP consumption taken for calculation Assesed cosumpion of 18855 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 446 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 446 * 5 HP = 2230 HP - 446 * 8 HP = 3568 HP ) = 1338 HP 265.52466367713 Units per HP consumption taken for calculation Assesed cosumpion of 18855 units will bring down the T&D less then the 10% | *Proposed to byfergate the IP load to the respective IP feeder *Proposed reconductpring of HT and LT lines in the Feeder *Proposed to byfurcate the IP set from the Domestic feeder to agri feeder in RDSS *proposed vigilence activity in the Judistriction *proposed to replace the Electromechanical to Electrostatic in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 446 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 446 * 5 HP = 2230 HP - 446 * 8 HP = 3568 HP ) = 1338 HP 265.52466367713 Units per HP consumption taken for calculation Assesed cosumpion of 18855 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 446 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 446 * 5 HP = 2230 HP - 446 * 8 HP = 3568 HP ) = 1338 HP 265.52466367713 Units per HP consumption taken for calculation Assesed cosumpion of 18855 units will bring down the T&D less then the 10%
17 | NON RAPDRP | THALLAK | DODDAULLARTHI | MYLANAHALLI_66 | F08-GUDIHALLI | MYLANAHALLI_66F08-GUDIHALLI | 1310402901020303 | AGRI | 23.75 | 14.68 | 38.43 | 112 | 0 | 395 | 522.17 | 506.78 | 506.78 | 0 | 15.39 | 20000 | 307800 | 0.414 | 307800 | 0 | 0 | 0 | 0 | 160000 | 160000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 467800 |  |  | 0 | 0 | 0 | 423358.519 | 423358.519 | 44441.481 | 9.5001 | 9.5 | 0.00010282 | 5-10 | 90.4999 | 90.4999 | 2177495.81 | 2463946.429 | 2463946.61 | 2177495.69 | 100 | 9.5001 | 9.5001 | 5-10 | 100 | 9.5001 | 5-10 |  | 423358.519 | 9.5001 | 5-10
18 | NON RAPDRP | THALLAK | THALLAK | MYLANAHALLI_66 | F09-KD KOTE | MYLANAHALLI_66F09-KD KOTE | 1310402901010106 | AGRI | 19.35 | 18.46 | 38.43 | 79 | 17 | 266 | 944.367 | 921.97 | 921.97 | 0 | 22.397 | 20000 | 447940 | 0.82907 | 447940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105000 | 105000 | 0 | 0 | 0 | 342940 |  |  | 0 | 0 | 299 | 289800 | 290099 | 52841 | 15.4082 | 15.41 | -0.0017653 | 15-20 | 84.5918 | 85.0163 | 1711453 | 1690809.06 | 1690989.06 | 1711270.78 | 100.0106 | 15.3992 | 14.9746 | 15-20 | 100 | 14.9837 | 10-15 | 1456 | 291555 | 14.9837 | 10-15 | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 266 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 266 * 5 HP = 1330 HP - 266 * 8 HP = 2128 HP ) = 798 HP 257.849624060149 Units per HP consumption taken for calculation Assesed cosumpion of 1456 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 266 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 266 * 5 HP = 1330 HP - 266 * 8 HP = 2128 HP ) = 798 HP 257.849624060149 Units per HP consumption taken for calculation Assesed cosumpion of 1456 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 266 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 266 * 5 HP = 1330 HP - 266 * 8 HP = 2128 HP ) = 798 HP 257.849624060149 Units per HP consumption taken for calculation Assesed cosumpion of 1456 units will bring down the T&D less then the 10% | *Proposed to byfergate the IP load to the respective IP feeder *Proposed reconductpring of HT and LT lines in the Feeder *Proposed to byfurcate the IP set from the Domestic feeder to agri feeder in RDSS *proposed vigilence activity in the Judistriction *proposed to replace the Electromechanical to Electrostatic in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 266 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 266 * 5 HP = 1330 HP - 266 * 8 HP = 2128 HP ) = 798 HP 257.849624060149 Units per HP consumption taken for calculation Assesed cosumpion of 1456 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 266 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 266 * 5 HP = 1330 HP - 266 * 8 HP = 2128 HP ) = 798 HP 257.849624060149 Units per HP consumption taken for calculation Assesed cosumpion of 1456 units will bring down the T&D less then the 10%
19 | NON RAPDRP | THALLAK | DODDAULLARTHI | MYLANAHALLI_66 | F10-GHATAPARTHI | MYLANAHALLI_66F10-GHATAPARTHI | 1310402901010107 | NJY | 26.58 | 16.55 | 43.13 | 46 | 2366 | 0 | 6001.8 | 5896.8 | 5896.8 | 0 | 105 | 2000 | 210000 | 0.82907 | 210000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 20000 | 0 | 0 | 0 | 190000 |  |  | 0 | 0 | 167830.5 | 0 | 167830.5 | 22169.5 | 11.6682 | 11.67 | -0.0018421 | 10-15 | 88.3318 | 88.3318 | 23521830 | 1750089.68 | 1022758.75 | 24249160.93 | 58.4404 | 48.3786 | 48.3786 | >30 | 58.4404 | 48.3786 | >30 |  | 167830.5 | 11.6682 | 10-15
20 | NON RAPDRP | THALLAK | DODDAULLARTHI | MYLANAHALLI_66 | F11-KAMASAMUDRA NJY | MYLANAHALLI_66F11-KAMASAMUDRA NJY | 1310402901020304 | NJY | 21.65 | 21.0825 | 42.7325 | 87 | 3168 | 0 | 11107.6 | 10979.3 | 10979.3 | 0 | 128.3 | 2000 | 256600 | 0.414 | 256600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256600 |  |  | 0 | 0 | 222709.2 | 0 | 222709.2 | 33890.8 | 13.2076 | 13.21 | -0.0023617 | 10-15 | 86.7924 | 86.7924 | 33507888 | 2341463.57 | 1287420.69 | 34561930.88 | 54.9836 | 52.2784 | 52.2784 | >30 | 54.9836 | 52.2784 | >30 |  | 222709.2 | 13.2076 | 10-15
21 | NON RAPDRP | THALLAK | DODDAULLARTHI | MYLANAHALLI_66 | F12-D.ULLARTHI | MYLANAHALLI_66F12-D.ULLARTHI | 1310402901020305 | AGRI | 22 | 20 | 42 | 118 | 0 | 585 | 575.647 | 545.655 | 545.655 | 0 | 29.992 | 20000 | 599840 | 0.414 | 599840 | 0 | 0 | 0 | 0 | 105000 | 105000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 704840 | 599840 | 105000 | 0 | 0 | 0 | 637578.487 | 637578.487 | 67261.513 | 9.5428 | 9.78 | -0.23719 | 5-10 | 90.4572 | 90.4572 | 2186662 | 3710791.382 | 3710791.451 | 2186662.04 | 100 | 9.5428 | 9.5428 | 5-10 | 100 | 9.5428 | 5-10 |  | 637578.487 | 9.5428 | 5-10
22 | NON RAPDRP | THALLAK | DODDAULLARTHI | MYLANAHALLI_66 | F13-KALUVEHALLI | MYLANAHALLI_66F13-KALUVEHALLI | 1310402901010109 | NJY | 21.74 | 17.29 | 39.03 | 55 | 2558 | 0 | 2202.75 | 2099.44 | 2099.44 | 0 | 103.31 | 2000 | 206620 | 0.82907 | 206620 | 0 | 0 | 0 | 0 | 40000 | 40000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246620 |  |  | 0 | 0 | 211634 | 0 | 211634 | 34986 | 14.1862 | 14.19 | -0.0038026 | 10-15 | 85.8138 | 85.8138 | 21083301 | 2990540.7 | 2589711.21 | 21484130.49 | 86.5968 | 25.688 | 25.688 | 20-30 | 86.5968 | 25.688 | 20-30 |  | 211634 | 14.1862 | 10-15
23 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NAYAKANAHATTI_66 | F01-DRDO | NAYAKANAHATTI_66F01-DRDO | 1310402908010104 | DEFENSE ESTABLISHMENT | 11.5 | 0.93 | 12.43 | 3 | 5 | 0 | 440.102 | 430.238 | 430.238 | 0 | 9.864 | 10000 | 98640 | 1.3326 | 98640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98640 |  |  | 0 | 0 | 98459 | 0 | 98459 | 181 | 0.1835 | 0.18 | 0.0034955 | 0-5 | 99.8165 | 99.8165 | 4301 | 940059 | 940813 | 3547 | 100.0802 | 0.10343 | 0.10343 | 0-5 | 100 | 0.1835 | 0-5 |  | 98459 | 0.1835 | 0-5
24 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NAYAKANAHATTI_66 | F02-DEVARAHATTY | NAYAKANAHATTI_66F02-DEVARAHATTY | 1310402908020303 | AGRI | 22.84 | 16.2825 | 39.1225 | 98 | 5 | 425 | 909.914 | 892.837 | 892.837 | 0 | 17.077 | 20000 | 341540 | 1.3326 | 341540 | 0 | 0 | 0 | 0 | 60000 | 60000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401540 |  |  | 0 | 0 | 46 | 363348.64 | 363394.64 | 38145.36 | 9.4998 | 9.5 | -0.0002341 | 5-10 | 90.5002 | 90.5002 | 1926947 | 2116831.879 | 2115657.14 | 1928121.5 | 99.9445 | 9.55 | 9.55 | 5-10 | 99.9445 | 9.55 | 5-10 |  | 363394.64 | 9.4998 | 5-10
25 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NAYAKANAHATTI_66 | F03-NERLAGUNTE | NAYAKANAHATTI_66F03-NERLAGUNTE | 1310402908010103 | AGRI | 16.45 | 9.34 | 25.79 | 121 | 1 | 386 | 590.876 | 579.685 | 579.685 | 0 | 11.191 | 30000 | 335730 | 1.3326 | 335730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335730 |  |  | 0 | 0 | 33 | 303802.932 | 303835.932 | 31894.068 | 9.4999 | 9.5 | -8.3996e-05 | 5-10 | 90.5001 | 90.5001 | 1167833.84 | 1768485.517 | 1768475.405 | 1167846.07 | 99.9994 | 9.5004 | 9.5004 | 5-10 | 99.9994 | 9.5004 | 5-10 |  | 303835.932 | 9.4999 | 5-10
26 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NAYAKANAHATTI_66 | F04-MAHADEVAPURA | NAYAKANAHATTI_66F04-MAHADEVAPURA | 1310402908010102 | AGRI | 23.45 | 18.615 | 42.065 | 141 | 6 | 537 | 919.382 | 895.894 | 895.894 | 0 | 23.488 | 20000 | 469760 | 1.3326 | 469760 | 0 | 0 | 0 | 0 | 79000 | 79000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548760 |  |  | 0 | 0 | 622 | 496006.118 | 496628.118 | 52131.882 | 9.4999 | 9.5 | -5.7949e-05 | 5-10 | 90.5001 | 90.5001 | 1840899.67 | 2893563.477 | 2891146.272 | 1843316.98 | 99.9165 | 9.5755 | 9.5755 | 5-10 | 99.9165 | 9.5755 | 5-10 |  | 496628.118 | 9.4999 | 5-10
27 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NAYAKANAHATTI_66 | F05-GOWDIGERE | NAYAKANAHATTI_66F05-GOWDIGERE | 1310402908010101 | AGRI | 21.56 | 18.91 | 40.47 | 126 | 0 | 521 | 887.219 | 861.241 | 861.241 | 0 | 25.978 | 20000 | 519560 | 1.3326 | 519560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 519560 |  |  | 0 | 0 | 0 | 470200.44 | 470200.44 | 49359.56 | 9.5003 | 9.5 | 0.00026176 | 5-10 | 90.4997 | 90.4997 | 1924145.83 | 2736566.536 | 2736566.745 | 1924146.82 | 100 | 9.5003 | 9.5003 | 5-10 | 100 | 9.5003 | 5-10 |  | 470200.44 | 9.5003 | 5-10
28 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NAYAKANAHATTI_66 | F06-SARJAVVANAHALLI | NAYAKANAHATTI_66F06-SARJAVVANAHALLI | 1310402908010110 | AGRI | 0 | 0 | 0 | 0 | 0 | 0 | 35.563 | 23.818 | 23.818 | 0 | 11.745 | 20000 | 234900 | 1.3326 | 234900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234900 |  |  | 0 | 0 | 0 | 0 | 0 | 234900 | 100 | 100 | 0 | >30 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 100 | #DIV/0! | >30 | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | 100 | >30 | Newly created feeder tagging has to be done | Newly created feeder tagging has to be done | Newly created feeder tagging has to be done | Newly created feeder tagging has to be done | Newly created feeder tagging has to be done | Newly created feeder tagging has to be done
29 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NAYAKANAHATTI_66 | F07-GWORIPURA NJY | NAYAKANAHATTI_66F07-GWORIPURA NJY | 1310402908010107 | NJY | 17.68 | 18.7 | 36.38 | 88 | 2078 | 7 | 763.016 | 752.09 | 752.09 | 0 | 10.926 | 20000 | 218520 | 1.3326 | 218520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 232 | 0 | 0 | 0 | 218288 |  |  | 0 | 0 | 198795 | 6470.135 | 205265.135 | 13022.865 | 5.9659 | 5.97 | -0.0040903 | 5-10 | 94.0341 | 94.0341 | 24155463 | 1983257.015 | 1277212.485 | 24861507.53 | 64.3997 | 39.4423 | 39.4423 | >30 | 64.3997 | 39.4423 | >30 |  | 205265.135 | 5.9659 | 5-10 | [6 empty] | = | 0 | - | 8 | = | 0 | ) | = | 0 | HP | #DIV/0! | Units per HP consumption taken for calculation Assesed cosumpion of | 0 | units will bring down the T&D less then the 10% | #DIV/0! | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 20 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 20 * 5 HP = 100 HP - 20 * 8 HP = 160 HP ) = 60 HP 3272 Units per HP consumption taken for calculation Assesed cosumpion of 16586 units will bring down the T&D less then the 10%
30 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NAYAKANAHATTI_66 | F09-NAAYAKANAHATTY | NAYAKANAHATTI_66F09-NAAYAKANAHATTY | 1310402908020301 | DOMESTIC | 2.5 | 4.13 | 6.63 | 35 | 3697 | 20 | 857.779 | 842.322 | 842.322 | 0 | 15.457 | 20000 | 309140 | 0.4568 | 309140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309140 |  |  | 0 | 0 | 236761 | 19964.99 | 256725.99 | 52414.01 | 16.9548 | 16.95 | 0.004781 | 15-20 | 83.0452 | 85.1756 | 5506354 | 2928572.344 | 3309423.54 | 5125502.88 | 113.0047 | 6.155 | 3.7475 | 5-10 | 100 | 14.8244 | 10-15 | 6586 | 263311.99 | 14.8244 | 10-15 | Ther are 20 Nos of Authorised Ip sets connected in the NJY feeder whihc are need to by byfergated which are running 24Hours but the consumption calculated for 7Hrs power supply hence difference in consumption is assessed | Ther are 20 Nos of Authorised Ip sets connected in the NJY feeder whihc are need to by byfergated which are running 24Hours but the consumption calculated for 7Hrs power supply hence difference in consumption is assessed | Ther are 20 Nos of Authorised Ip sets connected in the NJY feeder whihc are need to by byfergated which are running 24Hours but the consumption calculated for 7Hrs power supply hence difference in consumption is assessed | *Proposed to byfergate the IP load to the respective IP feeder *Proposed reconductpring of HT and LT lines in the Feeder *Proposed to byfurcate the IP set from the Domestic feeder to agri feeder in RDSS *proposed vigilence activity in the Judistriction *proposed to replace the Electromechanical to Electrostatic in the feeder | Ther are 20 Nos of Authorised Ip sets connected in the NJY feeder whihc are need to by byfergated which are running 24Hours but the consumption calculated for 7Hrs power supply hence difference in consumption is assessed | Ther are 20 Nos of Authorised Ip sets connected in the NJY feeder whihc are need to by byfergated which are running 24Hours but the consumption calculated for 7Hrs power supply hence difference in consumption is assessed
31 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NAYAKANAHATTI_66 | F10-HALAJOGIHATTY NJY | NAYAKANAHATTI_66F10-HALAJOGIHATTY NJY | 1310402908010106 | NJY | 25.64 | 14.6725 | 40.3125 | 52 | 1097 | 0 | 906.99 | 891.264 | 891.264 | 0 | 15.726 | 10000 | 157260 | 0.4568 | 157260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157260 |  |  | 0 | 0 | 139193 | 0 | 139193 | 18067 | 11.4886 | 11.49 | -0.0013824 | 10-15 | 88.5114 | 88.5114 | 18855195 | 1270648.35 | 914632.35 | 19211211 | 71.9815 | 36.2881 | 36.2881 | >30 | 71.9815 | 36.2881 | >30 |  | 139193 | 11.4886 | 10-15
32 | NON RAPDRP | THALLAK | HIREHALLI | NAYAKANAHATTI_66 | F11-REKALAGERE | NAYAKANAHATTI_66F11-REKALAGERE | 1310402908020304 | AGRI | 18.68 | 21.625 | 40.305 | 138 | 17 | 401 | 406.49 | 225.06 | 225.06 | 0 | 181.43 | 3000 | 544290 | 0.4568 | 544290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79000 | 79000 | 0 | 0 | 0 | 465290 |  |  | 0 | 0 | 644 | 420442.67 | 421086.67 | 44203.33 | 9.5002 | 9.5 | 0.00016764 | 5-10 | 90.4998 | 90.4998 | 1020583.02 | 2453498.195 | 2452774.041 | 1021307.42 | 99.9705 | 9.5269 | 9.5269 | 5-10 | 99.9705 | 9.5269 | 5-10 |  | 421086.67 | 9.5002 | 5-10
33 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NAYAKANAHATTI_66 | F12-NELGETHNAHATTY | NAYAKANAHATTI_66F12-NELGETHNAHATTY | 1310402908020302 | AGRI | 19.86 | 21.733 | 41.593 | 132 | 0 | 359 | 254.21 | 95.56 | 95.56 | 0 | 158.65 | 3000 | 475950 | 0.4568 | 475950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 60000 | 0 | 0 | 0 | 415950 |  |  | 0 | 0 | 0 | 376434.56 | 376434.56 | 39515.44 | 9.5 | 9.5 | 4.5679e-05 | 5-10 | 90.5 | 90.5 | 903044 | 2190849.345 | 2190849.147 | 903044 | 100 | 9.5001 | 9.5001 | 5-10 | 100 | 9.5001 | 5-10 |  | 376434.56 | 9.5 | 5-10
34 | NON RAPDRP | THALLAK | HIREHALLI | NAYAKANAHATTI_66 | F13-TOREKOLAMMANAHALLY | NAYAKANAHATTI_66F13-TOREKOLAMMANAHALLY | 1310402908020305 | AGRI | 17.95 | 20.769 | 38.719 | 115 | 3 | 412 | 797.321 | 775.94 | 775.94 | 0 | 21.381 | 20000 | 427620 | 0.4568 | 427620 | 0 | 0 | 0 | 0 | 56000 | 56000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483620 |  |  | 0 | 0 | 46 | 437630.694 | 437676.694 | 45943.306 | 9.4999 | 9.5 | -0.00012282 | 5-10 | 90.5001 | 90.5001 | 2155337.01 | 2547709.682 | 2547385.528 | 2155661.08 | 99.9873 | 9.5114 | 9.5114 | 5-10 | 99.9873 | 9.5114 | 5-10 |  | 437676.694 | 9.4999 | 5-10
35 | NON RAPDRP | THALLAK | HIREHALLI | NAYAKANAHATTI_66 | F14-MALLURAHALLY | NAYAKANAHATTI_66F14-MALLURAHALLY | 1310402908020306 | AGRI | 19.64 | 12.36 | 32 | 121 | 2 | 304 | 756.409 | 735.9 | 735.9 | 0 | 20.509 | 20000 | 410180 | 0.4568 | 410180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56000 | 56000 | 0 | 0 | 0 | 354180 |  |  | 0 | 0 | 119 | 320413.2 | 320532.2 | 33647.8 | 9.5002 | 9.5 | 0.00019764 | 5-10 | 90.4998 | 90.4998 | 1508689 | 1865849.616 | 1865570.624 | 1508967.99 | 99.985 | 9.5137 | 9.5137 | 5-10 | 99.985 | 9.5137 | 5-10 |  | 320532.2 | 9.5002 | 5-10
36 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NAYAKANAHATTI_66 | F15-BEMAGONDANAHALLY NJY | NAYAKANAHATTI_66F15-BEMAGONDANAHALLY NJY | 1310402908010108 | NJY | 18.65 | 15.78 | 34.43 | 57 | 1109 | 0 | 558.254 | 548.44 | 548.44 | 0 | 9.814 | 20000 | 196280 | 0.4568 | 196280 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206280 |  |  | 0 | 0 | 175437 | 0 | 175437 | 30843 | 14.952 | 14.95 | 0.002007 | 10-15 | 85.048 | 85.048 | 32758529 | 2008288.36 | 1049762.36 | 33717055 | 52.2715 | 55.5441 | 55.5441 | >30 | 52.2715 | 55.5441 | >30 |  | 175437 | 14.952 | 10-15 | [6 empty] | = | 0 | - | 8 | = | 0 | ) | = | 0 | HP | #DIV/0! | Units per HP consumption taken for calculation Assesed cosumpion of | 0 | units will bring down the T&D less then the 10% | #DIV/0! | #DIV/0!
37 | NON RAPDRP | THALLAK | HIREHALLI | NAYAKANAHATTI_66 | F16-THIPPERUDRASWAMY NJY | NAYAKANAHATTI_66F16-THIPPERUDRASWAMY NJY | 1310402908020101 | NJY | 17.98 | 20.45 | 38.43 | 44 | 720 | 0 | 253.535 | 253.16 | 253.16 | 0 | 0.375 | 20000 | 7500 | 0.4568 | 7500 | 0 | 0 | 0 | 0 | 110879 | 110879 | 0 | 0 | 0 | 0 | 10000 | 10000 | 0 | 0 | 0 | 108379 |  |  | 0 | 0 | 97097 | 0 | 97097 | 11282 | 10.4098 | 10.41 | -0.00023427 | 10-15 | 89.5902 | 89.5902 | 18241432 | 958361.98 | 408845.98 | 18790948 | 42.6609 | 61.78 | 61.78 | >30 | 42.6609 | 61.78 | >30 |  | 97097 | 10.4098 | 10-15
38 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NAYAKANAHATTI_66 | F17-KSSIDC | NAYAKANAHATTI_66F17-KSSIDC | 1310402908010109 | INDUSTRIAL | 8 | 0 | 8 | 18 | 2 | 0 | 1.1 | 1.1 | 0 | 1.1 | 0 | 2000 | 0 | 0.4568 | 0 | 0 | 0 | 0 | 0 | 232 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 |  |  | 0 | 0 | 232 | 0 | 232 | 0 | 0 | 0 | 0 | 0-5 | 100 | 100 | -1093 | 4322 | 4320 | -1091 | 99.9537 |  | 0.046275 | NA | 99.9537 | 0.046275 | 0-5 |  | 232 | 0 | 0-5
39 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NERALAGUNTE_66 | F01-BHEEMANAKERE | NERALAGUNTE_66F01-BHEEMANAKERE | 1310404905010103 | AGRI | 11.24 | 8.19 | 19.43 | 88 | 2 | 259 | 3843.6 | 3769.5 | 3769.5 | 0 | 74.1 | 2000 | 148200 | 0.6546 | 148200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148200 |  |  | 0 | 0 | 56 | 134065.341 | 134121.341 | 14078.659 | 9.4998 | 9.5 | -0.00023009 | 5-10 | 90.5002 | 90.5002 | 6981402.96 | 781482.267 | 781482.267 | 6981403.3 | 100 | 9.4998 | 9.4998 | 5-10 | 100 | 9.4998 | 5-10 |  | 134121.341 | 9.4998 | 5-10
40 | NON RAPDRP | THALLAK | THALLAK | NERALAGUNTE_66 | F02-HOSAHALLY | NERALAGUNTE_66F02-HOSAHALLY | 1310404905010104 | NJY | 9.8 | 12.83 | 22.63 | 32 | 828 | 0 | 3445.9 | 3394.5 | 3394.5 | 0 | 51.4 | 1000 | 51400 | 0.6546 | 51400 | 0 | 0 | 0 | 0 | 52000 | 52000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103400 |  |  | 0 | 0 | 92033.2 | 0 | 92033.2 | 11366.8 | 10.993 | 10.99 | 0.0030368 | 10-15 | 89.007 | 89.007 | 13452561 | 891783.81 | 542687 | 13801657.81 | 60.8541 | 45.8356 | 45.8356 | >30 | 60.8541 | 45.8356 | >30 |  | 92033.2 | 10.993 | 10-15
41 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NERALAGUNTE_66 | F03-YARAMANCHAIAHNAHATTY | NERALAGUNTE_66F03-YARAMANCHAIAHNAHATTY | 1310404905010101 | AGRI | 16.58 | 15.85 | 32.43 | 34 | 1 | 225 | 7423.3 | 7394.5 | 7394.5 | 0 | 28.8 | 1000 | 28800 | 0.6546 | 28800 | 0 | 0 | 0 | 0 | 180000 | 180000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208800 |  |  | 0 | 0 | 64 | 188900.048 | 188964.048 | 19835.952 | 9.5 | 9.5 | -2.2989e-05 | 5-10 | 90.5 | 90.5 | 655071.87 | 1103354.17 | 1099398.238 | 659028.02 | 99.6415 | 9.8245 | 9.8245 | 5-10 | 99.6415 | 9.8245 | 5-10 |  | 188964.048 | 9.5 | 5-10
42 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NERALAGUNTE_66 | F04-KANIVE MARAMMA NJY | NERALAGUNTE_66F04-KANIVE MARAMMA NJY | 1310404905010102 | NJY | 10.25 | 9.18 | 19.43 | 33 | 1015 | 4 | 6675.3 | 6516.9 | 6516.9 | 0 | 158.4 | 1000 | 158400 | 0.6546 | 158400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158400 |  |  | 0 | 0 | 135163 | 4251.803 | 139414.803 | 18985.197 | 11.9856 | 11.99 | -0.0043958 | 10-15 | 88.0144 | 88.0144 | 25492841 | 1413386.663 | 716961.663 | 26189266 | 50.7265 | 55.3534 | 55.3534 | >30 | 50.7265 | 55.3534 | >30 |  | 139414.803 | 11.9856 | 10-15
43 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NERALAGUNTE_66 | F05-BHATTAIAHNAHATTI | NERALAGUNTE_66F05-BHATTAIAHNAHATTI | 1310404905010106 | AGRI | 10 | 20 | 30 | 115 | 0 | 142 | 2183 | 2015.8 | 2015.8 | 0 | 167.2 | 2000 | 334400 | 0.6546 | 334400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180000 | 180000 | 0 | 0 | 0 | 154400 |  |  | 0 | 0 | 0 | 139732.188 | 139732.188 | 14667.812 | 9.4999 | 9.5 | -0.00012176 | 5-10 | 90.5001 | 90.5001 | 696998 | 813241.365 | 813241.365 | 696998 | 100 | 9.4999 | 9.4999 | 5-10 | 100 | 9.4999 | 5-10 |  | 139732.188 | 9.4999 | 5-10
44 | NON RAPDRP | THALLAK | NAYAKANAHATTI | NERALAGUNTE_66 | F06-KATAVVANAHALLY | NERALAGUNTE_66F06-KATAVVANAHALLY | 1310404905010105 | AGRI | 16 | 17 | 33 | 48 | 1 | 150 | 2256.3 | 2172.7 | 2172.7 | 0 | 83.6 | 2000 | 167200 | 0.6546 | 167200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167200 |  |  | 0 | 0 | 481 | 150835.348 | 151316.348 | 15883.652 | 9.4998 | 9.5 | -0.00020813 | 5-10 | 90.5002 | 90.5002 | 468333 | 883095.671 | 883261.674 | 468167.04 | 100.0188 | 9.4828 | 9.4828 | 5-10 | 100 | 9.4998 | 5-10 |  | 151316.348 | 9.4998 | 5-10
45 | NON RAPDRP | THALLAK | THALLAK | THALLAK_66 | F01-DEVARAHALLI | THALLAK_66F01-DEVARAHALLI | 1310403905020301 | AGRI | 18.64 | 19.8665 | 38.5065 | 96 | 1 | 339 | 427.518 | 416.822 | 416.822 | 0 | 10.696 | 20000 | 213920 | 0.2588 | 213920 | 0 | 0 | 0 | 0 | 185000 | 185000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398920 |  |  | 0 | 0 | 25 | 360998.241 | 361023.241 | 37896.759 | 9.4998 | 9.5 | -0.00016068 | 5-10 | 90.5002 | 90.5002 | 9468186.26 | 2102030.707 | 2102059.707 | 9468156.99 | 100.0014 | 9.4986 | 9.4986 | 5-10 | 100 | 9.4998 | 5-10 |  | 361023.241 | 9.4998 | 5-10
46 | NON RAPDRP | THALLAK | THALLAK | THALLAK_66 | F02-NKHATTI | THALLAK_66F02-NKHATTI | 1310403905020302 | AGRI | 21.48 | 13.02 | 34.5 | 77 | 1 | 313 | 595.396 | 578.144 | 578.144 | 0 | 17.252 | 20000 | 345040 | 0.2588 | 345040 | 0 | 0 | 0 | 0 | 40000 | 40000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385040 |  |  | 0 | 0 | 2 | 348458.88 | 348460.88 | 36579.12 | 9.5001 | 9.5 | 8.3108e-05 | 5-10 | 90.4999 | 90.4999 | 7589223 | 2028288.718 | 2028030.718 | 7589483.43 | 99.9873 | 9.5116 | 9.5116 | 5-10 | 99.9873 | 9.5116 | 5-10 |  | 348460.88 | 9.5001 | 5-10
47 | NON RAPDRP | THALLAK | THALLAK | THALLAK_66 | F03-BRHALLI | THALLAK_66F03-BRHALLI | 1310403905020303 | AGRI | 21.65 | 13.35 | 35 | 113 | 6 | 294 | 388.535 | 379.462 | 379.462 | 0 | 9.073 | 40000 | 362920 | 0.2588 | 362920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362920 |  |  | 0 | 0 | 177 | 328265.74 | 328442.74 | 34477.26 | 9.5 | 9.5 | -3.8576e-05 | 5-10 | 90.5 | 90.5 | 7068758.69 | 1912877.155 | 1913371.155 | 7068264.55 | 100.0258 | 9.4766 | 9.4766 | 5-10 | 100 | 9.5 | 5-10 |  | 328442.74 | 9.5 | 5-10
48 | NON RAPDRP | THALLAK | THALLAK | THALLAK_66 | F04-VALSE | THALLAK_66F04-VALSE | 1310404906010101 | AGRI | 17.56 | 20.87 | 38.43 | 107 | 3 | 501 | 572.801 | 554.968 | 554.968 | 0 | 17.833 | 40000 | 713320 | 0.35185 | 713320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105000 | 105000 | 0 | 0 | 0 | 608320 |  |  | 0 | 0 | 67 | 550463.199 | 550530.199 | 57789.801 | 9.4999 | 9.5 | -9.8468e-05 | 5-10 | 90.5001 | 90.5001 | 10708643.11 | 3204825.16 | 3204584.16 | 10708880.65 | 99.9925 | 9.5067 | 9.5067 | 5-10 | 99.9925 | 9.5067 | 5-10 |  | 550530.199 | 9.4999 | 5-10
49 | NON RAPDRP | THALLAK | THALLAK | THALLAK_66 | F05-HIREHALLI | THALLAK_66F05-HIREHALLI | 1310404906010102 | AGRI | 17.98 | 19.02 | 37 | 116 | 1 | 330 | 861.277 | 838.461 | 838.461 | 0 | 22.816 | 20000 | 456320 | 0.35185 | 456320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47000 | 47000 | 0 | 0 | 0 | 409320 |  |  | 0 | 0 | 5 | 370430.529 | 370435.529 | 38884.471 | 9.4998 | 9.5 | -0.00022696 | 5-10 | 90.5002 | 90.5002 | 6550900.01 | 2156068.573 | 2155905.573 | 6551061.74 | 99.9924 | 9.5066 | 9.5066 | 5-10 | 99.9924 | 9.5066 | 5-10 |  | 370435.529 | 9.4998 | 5-10
50 | NON RAPDRP | THALLAK | THALLAK | THALLAK_66 | F06-CHIKKAMMANAHALLI | THALLAK_66F06-CHIKKAMMANAHALLI | 1310404906010103 | AGRI | 22.65 | 15.5865 | 38.2365 | 60 | 9 | 395 | 112.48 | 98.61 | 98.61 | 0 | 13.87 | 20000 | 277400 | 0.35185 | 277400 | 0 | 0 | 0 | 0 | 198000 | 198000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475400 |  |  | 0 | 0 | 1082 | 429155.32 | 430237.32 | 45162.68 | 9.4999 | 9.5 | -6.7312e-05 | 5-10 | 90.5001 | 90.5001 | 9274582.62 | 2511224.843 | 2504528.843 | 9281279.03 | 99.7334 | 9.7412 | 9.7412 | 5-10 | 99.7334 | 9.7412 | 5-10 |  | 430237.32 | 9.4999 | 5-10
51 | NON RAPDRP | THALLAK | THALLAK | THALLAK_66 | F07-THALLAK | THALLAK_66F07-THALLAK | 1310403905020304 | NJY | 23.75 | 11.68 | 35.43 | 37 | 1934 | 1 | 462.396 | 453.807 | 453.807 | 0 | 8.589 | 20000 | 171780 | 0.2588 | 171780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171780 |  |  | 0 | 0 | 162924.8 | 55 | 162979.8 | 8800.2 | 5.1229 | 5.12 | 0.002948 | 5-10 | 94.8771 | 94.8771 | 15600039 | 1659315.29 | 1087552.76 | 16171801.53 | 65.5423 | 37.8154 | 37.8154 | >30 | 65.5423 | 37.8154 | >30 |  | 162979.8 | 5.1229 | 5-10
52 | NON RAPDRP | THALLAK | HIREHALLI | THALLAK_66 | F10-BUKKLARAHALLI | THALLAK_66F10-BUKKLARAHALLI | 1310404906010108 | AGRI | 16 | 14.71 | 30.71 | 115 | 1 | 428 | 1757.25 | 1552.37 | 1552.37 | 0 | 204.88 | 2000 | 409760 | 0.35185 | 409760 | 0 | 0 | 0 | 0 | 148300 | 148300 | 0 | 0 | 0 | 0 | 33000 | 33000 | 0 | 0 | 0 | 525060 |  |  | 0 | 0 | 14 | 469800 | 469814 | 55246 | 10.5218 | 10.52 | 0.0018451 | 10-15 | 89.4782 | 89.4782 | 10378291.01 | 2734450.37 | 2734450.37 | 10378293.8 | 100 | 10.5218 | 10.5218 | 10-15 | 100 | 10.5218 | 10-15 |  | 469814 | 10.5218 | 10-15
53 | NON RAPDRP | THALLAK | THALLAK | THALLAK_66 | F11-RUDRAMMANNAHALLY | THALLAK_66F11-RUDRAMMANNAHALLY | 1310403905020305 | NJY | 26.58 | 13.42 | 40 | 60 | 1307 | 0 | 656.182 | 648.189 | 648.189 | 0 | 7.993 | 20000 | 159860 | 0.2588 | 159860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159860 |  |  | 0 | 0 | 146949.7 | 0 | 146949.7 | 12910.3 | 8.076 | 8.08 | -0.003996 | 5-10 | 91.924 | 91.924 | 15308759 | 1417765.49 | 803517.49 | 15923007 | 56.6749 | 47.9021 | 47.9021 | >30 | 56.6749 | 47.9021 | >30 |  | 146949.7 | 8.076 | 5-10
54 | NON RAPDRP | THALLAK | THALLAK | THALLAK_66 | F12-BANJIGERE | THALLAK_66F12-BANJIGERE | 1310404906010107 | NJY | 21.74 | 17.29 | 39.03 | 56 | 1888 | 0 | 838.792 | 821.09 | 821.09 | 0 | 17.702 | 10000 | 177020 | 0.35185 | 177020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177020 |  |  | 0 | 0 | 153585.2 | 0 | 153585.2 | 23434.8 | 13.2385 | 13.24 | -0.0014959 | 10-15 | 86.7615 | 86.7615 | 17255764 | 1515042.1 | 918136.7 | 17852669.4 | 60.6014 | 47.4213 | 47.4213 | >30 | 60.6014 | 47.4213 | >30 |  | 153585.2 | 13.2385 | 10-15
55 | NON RAPDRP | THALLAK | THALLAK | THALLAK_66 | F15-MARUTHINAGARA | THALLAK_66F15-MARUTHINAGARA | 1310404906010104 | AGRI | 10.15 | 7.3 | 17.45 | 30 | 3 | 94 | 992.288 | 982.31 | 982.31 | 0 | 9.978 | 20000 | 199560 | 0.2588 | 199560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 85000 | 0 | 0 | 0 | 114560 |  |  | 0 | 0 | 1198 | 102478.686 | 103676.686 | 10883.314 | 9.5001 | 9.5 | 9.9511e-05 | 5-10 | 90.4999 | 90.4999 | 2147596.01 | 609295.929 | 596425.929 | 2160465.94 | 97.8877 | 11.4117 | 11.4117 | 10-15 | 97.8877 | 11.4117 | 10-15 |  | 103676.686 | 9.5001 | 5-10
56 | NON RAPDRP | THALLAK | HIREHALLI | THALLAK_66 | F16-CHAMUNDESHWARI | THALLAK_66F16-CHAMUNDESHWARI | 1310403905020306 | NJY | 14.5 | 12.6 | 39.03 | 43 | 1559 | 0 | 1196.18 | 1130.49 | 1130.49 | 0 | 65.69 | 2000 | 131380 | 0.2588 | 131380 | 0 | 0 | 0 | 0 | 64764 | 64764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196144 |  |  | 0 | 0 | 173003.4 | 0 | 173003.4 | 23140.6 | 11.7978 | 11.8 | -0.0022392 | 10-15 | 88.2022 | 88.2022 | 23413711 | 1745200.28 | 1156682.28 | 24002229 | 66.2779 | 41.5414 | 41.5414 | >30 | 66.2779 | 41.5414 | >30 |  | 173003.4 | 11.7978 | 10-15
57 | NON RAPDRP | THALLAK | DODDAULLARTHI | VISHWESHWARAPURA_66 | F03-GOWDRAHATTI | VISHWESHWARAPURA_66F03-GOWDRAHATTI | 1310402909010104 | AGRI | 10.25 | 9.75 | 20 | 52 | 2 | 478 | 8457.2 | 8232.1 | 8232.1 | 0 | 225.1 | 2000 | 450200 | 1 | 450200 | 0 | 0 | 0 | 0 | 106000 | 106000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556200 | 450200 | 106000 | 0 | 0 | 0 | 501817.204 | 501817.204 | 54382.796 | 9.7776 | 10.97 | -1.1924 | 5-10 | 90.2224 | 90.2224 | 1951549 | 2921890.173 | 2921609.171 | 1951830.35 | 99.9904 | 9.7862 | 9.7862 | 5-10 | 99.9904 | 9.7862 | 5-10 |  | 501817.204 | 9.7776 | 5-10 | Due to difference in the total sales of the Feeder in RR no wise Energy audit report and feederwise energy audit report T&D loss of the Generated and Energy audit report Format is different i.e, sale in RR no wise energy audi treport is 501877 units and sales in feeder wise energy auidit is 495177 units the difference of 6639 units lead the difference in the T&D loss
58 | NON RAPDRP | THALLAK | DODDAULLARTHI | VISHWESHWARAPURA_66 | F04-CHIKKA ULLARTHI | VISHWESHWARAPURA_66F04-CHIKKA ULLARTHI | 1310402909010103 | AGRI | 10.14 | 7.86 | 18 | 43 | 1 | 125 | 4933.1 | 4712.8 | 4712.8 | 0 | 220.3 | 2000 | 440600 | 1 | 440600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106000 | 106000 | 0 | 0 | 0 | 334600 |  |  | 0 | 0 | 14 | 144300 | 144314 | 190286 | 56.8697 | 56.87 | -0.00030484 | >30 | 43.1303 | 85.1285 | 420130.93 | 840049 | 840177 | 420002.97 | 100.0152 | 56.8631 | 14.8585 | >30 | 100 | 14.8715 | 10-15 | 140526 | 284840 | 14.8715 | 10-15 | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 125 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 125 * 5 HP = 625 HP - 125 * 8 HP = 1000 HP ) = 375 HP 535.360000000001 Units per HP consumption taken for calculation Assesed cosumpion of 140526 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 125 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 125 * 5 HP = 625 HP - 125 * 8 HP = 1000 HP ) = 375 HP 535.360000000001 Units per HP consumption taken for calculation Assesed cosumpion of 140526 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 125 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 125 * 5 HP = 625 HP - 125 * 8 HP = 1000 HP ) = 375 HP 535.360000000001 Units per HP consumption taken for calculation Assesed cosumpion of 140526 units will bring down the T&D less then the 10% | *Proposed to byfergate the IP load to the respective IP feeder *Proposed reconductpring of HT and LT lines in the Feeder *Proposed to byfurcate the IP set from the Domestic feeder to agri feeder in RDSS *proposed vigilence activity in the Judistriction *proposed to replace the Electromechanical to Electrostatic in the feeder | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 125 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 125 * 5 HP = 625 HP - 125 * 8 HP = 1000 HP ) = 375 HP 535.360000000001 Units per HP consumption taken for calculation Assesed cosumpion of 140526 units will bring down the T&D less then the 10% | per HP consumption is greater than the subdivision average agri consumption, Connected load of IP Sets is greater than the Sanction load there are 125 Nos of IP Sets with 5HP sanctioned Load but in field they are using average of 8HP connected load difference in the Sacntioned load and Conected load is ( 125 * 5 HP = 625 HP - 125 * 8 HP = 1000 HP ) = 375 HP 535.360000000001 Units per HP consumption taken for calculation Assesed cosumpion of 140526 units will bring down the T&D less then the 10%