## consumption
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Energy consumption & Peak load statement of 66/11 KV MUSS Chelur for the month of JANUARY - 2026
Sl No |  | Name of the Bank/Feeder | Category of feeder | Meter Serial Numbers | Meter Make | Meter CT ratio | Final Reading | Initial Reading | Difference | Meter constant | Energy consumption | TOTAL consumption | CT Ratio | Peak load
[14 empty] | AMP | MW | DATE | TIME
1 | L1 | 66kV Somanathpura - Chelur LINE-1 (Import) |  | 12527046 | L&T | 400/1 | 71997 | 70652 | 1345 | 2000 | 2690000 | 2322000 | 400/1 | 182 | 18.2 | 2026-01-24 | 0.375
|  | 66kV Somanathpura - Chelur LINE-1 (Export) |  |  |  |  | 252357 | 252173 | 184 | 2000 | 368000
2 | L2 | SOLAR LINE-2 (Export) | IPP | 23008376 | L&T | 200/1 | 4.388 | 4.234 | 0.154 | 120000 | 18480 | 2959560 | 200/1 | 140 | 16 | 2026-01-18 | 0.5
|  | SOLAR LINE-2 (Import) |  |  |  |  | 748.33 | 723.513 | 24.817 | 120000 | 2978040 |  |  | 9 | 1 | 2026-01-04 | 0.29167
3 | L3 | 66kV Chelur-Chakavelu LINE-3(Export) |  | X1876848 | SECURE | 400/1 | 46794 | 44860 | 1934 | 2000 | 3868000 | 3868000 | 400/1 | 128 | 12.8 | 2026-01-23 | 0.45833
|  | 66kV Chelur-Chakavelu LINE-3 (Import) |  |  |  |  | 2 | 2 | 0 | 2000 | 0
4 | T1 | TRANSFORMER-1(Export) |  | Q0469707 | SECURE | - /1A | 123.142 | 121.9 | 1.242 | 60000 | 74520 | 492960 | 100/1 | 51 | 5.1 | 2026-01-15 | 0.41667
|  | TRANSFORMER-1(Import) |  |  |  |  | 412.416 | 402.958 | 9.458 | 60000 | 567480
5 | T2 | TRANSFORMER-2(Export) |  | X1876847 | SECURE | 100/1 | 30433.4 | 29462 | 971.4 | 1000 | 971400 | 914200 | 100/1 | 67 | 6.7 | 2026-01-24 | 10:00
|  | TRANSFORMER-2(Import) |  |  |  |  | 617.6 | 560.4 | 57.2 | 1000 | 57200
6 | B1 | BANK-1 (Export) |  | Q0769213 | SECURE | 1 | 202.5 | 177.4 | 25.1 | 3000 | 75300 | 481500 | 600/1 | 304 | 5.0667 | 2026-01-15 | 0.41667
|  | BANK-1 (Import) |  |  |  |  | 687.4 | 501.8 | 185.6 | 3000 | 556800
7 | f8 | F8-MUGIREDDYPALLI (Export) | NJY | Q0257867 | SECURE | 1 | 45.916 | 37.148 | 8.768 | 20000 | 175360 | 175360 | 200/1 | 36 | 0.6 | 2026-01-14 | 0.33333
|  | F8-MUGIREDDYPALLI (Import) |  |  |  |  | 0 | 0 | 0 | 20000 | 0
8 | f9 | F9- BAJJAPURA (Export) | Agri | Q0254986 | SECURE | 1 | 214.467 | 204.342 | 10.125 | 20000 | 202500 | 202500 | 200/1 | 78 | 1.3 | 2026-01-21 | 0.5
|  | F9-BAJJAPURA (Import) |  |  |  |  | 0 | 0 | 0 | 20000 | 0
9 | f10 | F10-GUNDLAPALLI (Export) | Agri | Q0246266 | SECURE | 1 | 848.273 | 820.65 | 27.623 | 20000 | 552460 | 552460 | 200/1 | 200 | 3.3333 | 2026-01-16 | 0.41667
|  | F10-GUNDLAPALLI (Import) |  |  |  |  | 0 | 0 | 0 | 20000 | 0
10 | F4 | F4- NALLAGUTLAPALLI (Export) | Agri | 12527037 | L&T | 1 | 58218.9 | 57746 | 472.9 | 500 | 236450 | 236450 | 200/1 | 84 | 1.4 | 2026-01-29 | 0.375
|  | F4- NALLAGUTLAPALLI (Import) |  |  |  |  | 9255.9 | 9255.9 | 0 | 500 | 0
11 | F5 | F5- T VIJAY KUMAR SOLAR PLANT (Export) | IPP | 22011761 | L&T | 60/1A | 4.996 | 4.841 | 0.155 | 6000 | 930 | 135480 | 100/1 | 48 | 0.8 | 2026-01-29 | 0.5
|  | F5- T VIJAY KUMAR SOLAR PLANT (Import) |  |  |  |  | 719.436 | 696.701 | 22.735 | 6000 | 136410 |  |  | 3 | 0.05 | 2026-01-12 | 0.33333
12 | F7 | F7 - HOMBALE CONSTRUCTIONS & ESTATES PVT. LTD.(Export) | IPP | 22011731 | L&T | 250/1A | 3.794 | 3.679 | 0.115 | 25000 | 2875 | 547125 | 400/1 | 172 | 2.8667 | 2026-12-22 | 0.45833
|  | F7 - HOMBALE CONSTRUCTIONS & ESTATES PVT. LTD. (Import) |  |  |  |  | 674.073 | 652.073 | 22 | 25000 | 550000 |  |  | 12 | 0.2 | 2026-01-01 | 0.70833
13 | B2 | BANK-2 (Export) |  | Q0575429 | SECURE | 1 | 626.6 | 568.7 | 57.9 | 1000 | 57900 | 905500 | 800/1 | 403 | 6.7167 | 2026-01-24 | 10:00
|  | BANK-2 (Import) |  |  |  |  | 30105.4 | 29142 | 963.4 | 1000 | 963400
14 | F1 | F1-NJY CHELUR (Export)) | NJY | Q0578382 | SECURE | 1 | 7516.51 | 7289.95 | 226.56 | 2000 | 453120 | 453120 | 200/1 | 68 | 1.1333 | 2026-01-23 | 0.33333
|  | F1-NJY CHELUR (Import)) |  |  |  |  | 0.09 | 0.09 | 0 | 2000 | 0
15 | F2 | F2-CHELUR EXPRESS (Export) | Agri | Q0578441 | SECURE | 1 | 5550.85 | 5429.1 | 121.75 | 4000 | 487000 | 487000 | 400/1 | 280 | 4.6667 | 2026-01-06 | 0.45833
|  | F2-CHELUR EXPRESS (Import) |  |  |  |  | 0.09 | 0.09 | 0 | 4000 | 0
16 | F3 | F3-VENKATAPURA (Export) | Agri | Q0578357 | SECURE | 1 | 2895.09 | 2763.11 | 131.98 | 2000 | 263960 | 263960 | 200/1 | 102 | 1.7 | 2026-01-21 | 0.45833
|  | F3-VENKATAPURA (Import) |  |  |  |  | 0.09 | 0.09 | 0 | 2000 | 0
17 | F11 | F11 -MACHANAHALLI (Export) | Agri | 12526784 | L&T | 1 | 173.3 | 0.6 | 172.7 | 2000 | 345400 | 0 | 200/1 | 164 | 2.7333 | 2026-01-20 | 10:00
17 | F11 | F11 -MACHANAHALLI (Import) |  |  |  |  | 4258.9 | 4258.9 | 0 | 2000 | 0 | 0 | 200/1 | - | 0 | - | -
20 | F12 | F12- ELSA Consultancy SOLAR PLANT (EXPORT) | IPP | 25004825 | L&T | 250/1A | 32.852 | 32.766 | 0.086 | 25000 | 2150 | 667225 | 400/1 | 200 | 3.3333 | 2026-01-22 | 0.5
|  | F12- ELSA Consultancy SOLAR PLANT (IMPORT) |  |  |  |  | 95.31 | 68.535 | 26.775 | 25000 | 669375 |  |  | 12 | 0.2 | 2026-01-05 | 0.70833
18 | CB-2 | CAPACITOR BANK -2 |  | Q0578392 | SECURE | 1 | 9.34 | 8.84 | 0.5 | 2000 | 1000 | 1000 | 200/1
19 | - | STATION AUX |  | 4954607 | ELSTER | - /5A | 21110.8 | 20951.7 | 159.1 | 10 | 1591 | 1591 | 50/5
Station Peak Load
[6 empty] | Peak in Amps |  | 653
[6 empty] | Peak Amps |  |  | Amps
[6 empty] | Peak in MW |  | 10.8833 | MW
[6 empty] | Hours |  | 0.375
[6 empty] | Dated |  | 2026-01-24
NET BANK =BANK-1 (IMPORT) + BANK-2 ( IMPORT)+ F-5T,VIJAY KUMAR SOLAR(IMPORT) +F-7 Hombale constructions & ESTATES PVT. LTD. SOLAR(IMPORT)F-12 ELSA (IMPORT) - BANK-1 (Export) - BANK-2 (EXPORT)
|  | TOTAL NET BANKS consumption | 2742785
NET FEEDERS =F1( EXPORT)+F2( EXPORT)+F3( EXPORT)+F4( EXPORT)+ F5 T,VIJAY KUMAR SOLAR(EXPORT) +F7 Hombale constructions & ESTATES PVT. LTD. SOLAR(EXPORT) F-12 ELSA (EXPORT)+STATION AUX+ F8 EXPORT +F9 EXPORT +F10 EXPORT+F-11 Machanahalli EXPORT
|  | TOTAL NET FEEDERS consumption | 2723796
Note 1 : F-11 MACHANAHALLI (AGRI) Feeder commissioned on 06-01-2026 at 16:50hrs IN Presence of AEE Bescom.

## Interruption
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Interruption Statement of 66/11 kV Chelur for the Month of JANUARY - 2026
SL. No. | Feeder No. and Name of the Feeder | Foreseen Interruption/ Line Clear |  | Unforeseen Interruption / Faulty |  | Scheduled Load shedding |  | Unscheduled Load shedding |  | Open Delta Power Supply |  | Three Phase Power Supply |  | 66kV Failure ( Main Supply) |  | OLR tripping
|  | No | Duration in hours | No | Duration in hours | No | Duration in hours | No | Duration in hours | No | Duration in hours | No | Duration in hours | No | Duration in hours | No | Duration in hours
1 | ABT meter 1(Bank I) | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ |  |  | _ | _
2 | F1-NJY CHELUR | 34 | 0.68056 | 14 | 0.055556 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 30.2396 | 3 | 0.024306 | 0 | 0
3 | F2-CHELUR EXPRESS | 28 | 0.55208 | 18 | 0.34375 | 142 | 16.1979 | 0 | 0 | 34 | 4.8333 | 64 | 9.0729 | 0 | 0 | 2 | 1:00
4 | F3-VENKATAPURA | 25 | 0.43403 | 17 | 0.18403 | 111 | 16.3333 | 0 | 0 | 32 | 5.0347 | 62 | 9.0139 | 0 | 0 | 0 | 0
5 | F4- NALLAGUTLAPALLI | 16 | 0.25 | 6 | 0.069444 | 104 | 16.5729 | 0 | 0 | 36 | 5.066 | 46 | 9.0417 | 0 | 0 | 0 | 0
6 | F8- MUGIREDDYPALLI | 21 | 0.375 | 7 | 0.076389 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 30.5243 | 3 | 0.024306 | 0 | 0
7 | F9- BAJJAPURA | 16 | 0.39931 | 11 | 0.21528 | 105 | 16.191 | 0 | 0 | 32 | 5.1528 | 84 | 9.0417 | 0 | 0 | 0 | 0
8 | F10- GUNDLAPALLI | 16 | 0.32292 | 22 | 0.29167 | 106 | 16.3958 | 0 | 0 | 34 | 4.9514 | 66 | 9.0382 | 0 | 0 | 1 | 3:55
9 | F11 - MACHANAHALLI | 18 | 0.47222 | 25 | 0.56597 | 98 | 12.9479 | 0 | 0 | 25 | 3.9514 | 61 | 7.3611 | 0 | 0 | 0 | 0

## F12
F12. Availability of 11/33/66/110/220 KV Lines for the month of January - 2026
Division | Station Name | Ref.Bus Voltage in kV | Scheduled |  |  | Unscheduled
|  |  | No.of Interruption | Duration in Minutes | % of Availability | No.of Interruption | Duration in Minutes | % of Availability
TL & SS Gowribidanur | 66/11kV Chelur | 11kV (F1) | 34 | 980 | 97.8047 | 17 | 115 | 99.7424
|  | 11kV (F2) | 170 | 24120 | 45.9677 | 18 | 495 | 98.8911
|  | 11kV (F3) | 136 | 24145 | 45.9117 | 17 | 265 | 99.4064
|  | 11kV (F4) | 120 | 24225 | 45.7325 | 6 | 100 | 99.776
|  | 11kV (F8) | 21 | 540 | 98.7903 | 10 | 145 | 99.6752
|  | 11kV (F9) | 121 | 23890 | 46.483 | 11 | 310 | 99.3056
|  | 11kV (F10) | 122 | 24075 | 46.0685 | 22 | 420 | 99.0591
|  | 11kV (F11) | 116 | 19325 | 56.7092 | 25 | 815 | 98.1743
* | No of Days of the month should be changed in Availability Formula

## F11
F11.Interruption statement for the month of JANUARY - 2026
Division | Station Name | Ref.Bus Voltage in kV | Feeder No | Interruptions due to Scheduled Load shedding |  | Interruptions due to Distribution |  |  |  | Interruptions due to transmission
[6 empty] | Scheduled |  | Unscheduled |  | Scheduled |  | Unscheduled
|  |  |  | No | Duration in minutes (Hrs*60+Min) | No | Duration in minutes (Hrs*60+Min) | No | Duration in minutes (Hrs*60+Min) | No | Duration in minutes (Hrs*60+Min) | No | Duration in minutes (Hrs*60+Min)
TL& SS Gowribidanur | 66/11 kV Chelur | 11 kV | F1 | 0 | 0 | 34 | 980 | 14 | 80 | 0 | 0 | 3 | 35
|  | 11 kV | F2 | 142 | 23325 | 28 | 795 | 18 | 495 | 0 | 0 | 0 | 0
|  | 11 kV | F3 | 111 | 23520 | 25 | 625 | 17 | 265 | 0 | 0 | 0 | 0
|  | 11 kV | F4 | 104 | 23865 | 16 | 360 | 6 | 100 | 0 | 0 | 0 | 0
|  | 11 kV | F8 | 0 | 0 | 21 | 540 | 7 | 110 | 0 | 0 | 3 | 35
|  | 11 kV | F9 | 105 | 23315 | 16 | 575 | 11 | 310 | 0 | 0 | 0 | 0
|  | 11 kV | F10 | 106 | 23610 | 16 | 465 | 22 | 420 | 0 | 0 | 0 | 0
|  | 11 kV | F11 | 98 | 18645 | 18 | 680 | 25 | 815 | 0 | 0 | 0 | 0

## Vital Parameter
Vital parameters for the sub-station for the JANUARY - 2026
66/11 kV MUSS, Chelur
Sl No | particulars | Capacity of Transformer/ Feeder |  | Peak Demand in MW |  |  |  |  | Energy in MU |  | Voltage Recorded in KV |  | Quantum of power supply in hrs |  |  |  | Interruption |  |  |  | Loading factor
|  |  |  | Normal |  | Contingency |  |  | Entitlement for the month | Actual Recording | Maximum | Minimum | Three phase |  | Open Delta |  | Scheduled |  | Unscheduled
|  | In A | In MW | [9 empty] | Scheduled | Actual | Scheduled | Actual | Nos | Duration in Hrs | Nos | Duration in Hrs
|  |  |  | In A | In MW | In A | In MW | In MW
1 | TRANSFORMER-1 | 68 | 6.8 | 51 | 5.1 | _ |  | _ | _ | 0.49296 | 67 | 61 | _ | _ | _ | _ | _ | _ | _ | _ | 1.3333
| TRANSFORMER-2 | 68 | 6.8 | 67 | 6.7 | _ |  | _ | _ | 0.9142 |  |  | - | - | - | - | - | - | - | - | 1.0149
2 | BANK-1 | 600 | 6.6 | 304 | 5.0667 | _ |  | _ | _ | 0.4815 | 11:07 | 11:00 | _ | _ | _ | _ | _ | _ | _ | _ | 1.9737
| BANK-2 | 800 | 0 | 403 | 6.7167 | _ |  | _ | _ | 0.9055 |  |  | - | - | - | - | - | - | - | - | 1.9851
3 | F1-NJY CHELUR | 200 | 3.3 | 68 | 1.1333 | _ |  | _ | _ | 0.45312 | _ | _ | 31 | 30.2396 | 0 | 0 | 34 | 0.68056 | 48 | 0.079861 | 2.9412
4 | F2-CHELUR EXPRESS | 200 | 3.3 | 280 | 4.6667 | _ |  | _ | _ | 0.487 | _ | _ | 9.0417 | 9.0729 | 5.1667 | 4.8333 | 170 | 16.75 | 50 | 0.38542 | 0.71429
5 | F3-VENKATAPURA | 200 | 3.3 | 200 | 3.3333 | _ |  | _ | _ | 0.26396 | _ | _ | 9.0417 | 9.0139 | 5.1667 | 5.0347 | 136 | 16.7674 | 49 | 0.18403 | 1
6 | F4- NALLAGUTLAPALLI | 200 | 3.3 | 84 | 1.4 | _ |  | _ | _ | 0.23645 | - | _ | 9.0417 | 9.0417 | 5.1667 | 5.066 | 120 | 16.8229 | 42 | 0.069444 | 2.381
7 | F8- MUGIREDDYPALLI | 200 | 3.3 | 36 | 0.6 | _ |  | _ | _ | 0.17536 | - | - | 31 | 30.5243 | 0 | 0 | 21 | 0.375 | 7 | 0.10069 | 5.5556
8 | F9-BAJJAPURA | 200 | 3.3 | 78 | 1.3 | _ |  | _ | _ | 0.2025 | - | - | 9.0417 | 9.0417 | 5.1667 | 5.1528 | 121 | 16.5903 | 43 | 0.21528 | 2.5641
9 | F10-GUNDLAPALLI | 200 | 3.3 | 200 | 3.3333 | _ |  | _ | _ | 0.55246 | - | - | 9.0417 | 9.0382 | 5.1667 | 4.9514 | 122 | 16.7188 | 56 | 0.45486 | 1
10 | F11- MACHANAHALLI | 200 | 3.3 | 164 | 2.7333 | _ |  | _ | _ | 0 | - | - | 9.0417 | 7.3611 | 5.1667 | 3.9514 | 116 | 13.4201 | 50 | 0.56597 | 1.2195
11 | Auxillary | 100 | 1.7 |  | - | _ |  | _ | _ | 0.001591 | _ | _
|  | Duration of maximum voltage beyond specified limits | [11 empty] | Nil
|  | Duration of minimum voltage beyond specified limits | [11 empty] | Nil

## B-FORM
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
B- FORMS OF IF POINTS
NAME OF THE STATION: 66/11kV Muss Chelur
NAME OF THE DIVISION: TL&SS Division Gowribidanur | [7 empty] | MONTH : JANUARY - 2026
Sl. No. | SUB-STATION NAME | PTR Capacity/Name of the EHT/ Name of the IPP with Voltage Class | INTERFACE POINT | METER TYPE | CT RATIO | METER SL.NO | FLOW TYPE | MF | INITIAL | FINAL | CONSUMPTION (IN KWH) | Remarks
1 | 66/11KV MUSS CHELUR |  | 11kV Bank-1 | DLMS/ SECURE | 600/1 | Q0769213 | FROM KPTCL | 3000 | 501.8 | 687.4 | 556800
[7 empty] | TO KPTCL | 3000 | 177.4 | 202.5 | 75300
2 |  |  | 11kV Bank-2 | DLMS/ SECURE | 800/1 | Q0575429 | FROM KPTCL | 1000 | 29142 | 30105.4 | 963400
[7 empty] | TO KPTCL | 1000 | 568.7 | 626.6 | 57900
3 |  |  | AUX-1 | ETV/ELSTER | 50/5 | 4954607 | TO KPTCL | 10 | 20951.7 | 21110.8 | 1591
4 |  |  | AUX-2 | [7 empty] | 0
5 |  | NIL | EHT | - | - | - | - | - | - | - | - | -
6 |  | ES SUN SOLAR | IPP | ETV/L&T | 200/1 | 23008376 | FROM KPTCL | 120000 | 4.234 | 4.388 | 18480
[7 empty] | TO KPTCL |  | 723.513 | 748.33 | 2978040
[8 empty] | Net Consumption |  |  | 2959560
7 |  | T VIJAY KUMAR | IPP | ETV/L&T | 60/1 | 22011761 | FROM KPTCL | 6000 | 4.841 | 4.996 | 930
[7 empty] | TO KPTCL |  | 696.701 | 719.436 | 136410
[8 empty] | Net Consumption |  |  | 135480 |  | 0.68074
8 |  | HOMBALE CONSTRUCTIONS & ESTATES PVT. LTD. | IPP | ETV/L&T | 250/1 | 22011731 | FROM KPTCL | 25000 | 3.679 | 3.794 | 2875
[7 empty] | TO KPTCL |  | 652.073 | 674.073 | 550000
[8 empty] | Net Consumption |  |  | 547125
9 |  | ELSA Consultancy SOLAR PLANT | IPP | ETV/L&T | 250/1 | 25004825 | FROM KPTCL | 25000 | 32.766 | 32.852 | 2150
[7 empty] | TO KPTCL |  | 68.535 | 95.31 | 669375
[8 empty] | Net Consumption |  |  | 667225
Transformer wise energy audit ANNEXURE
Sl. No. | SUB-STATION NAME | TRANSFORMER | Connected Bank | METER TYPE | CT RATIO | METER SL.NO | FLOW TYPE | MF | INITIAL | FINAL | CONSUMPTION
1 | 66/11kV Muss Chelur | 8 MVA TRANSFORMER-1 | Bank-1 | DLMS/ SECURE | 100/1 | Q0469707 | FROM KPTCL | 60000 | 402.958 | 412.416 | 567480
[7 empty] | TO KPTCL | 60000 | 121.9 | 123.142 | 74520
2 |  | 8 MVA TRANSFORMER-2 | Bank-2 | DLMS/ SECURE | 100/1 | X1876847 | FROM KPTCL | 1000 | 29462.3 | 30433.4 | 971100
[7 empty] | TO KPTCL | 1000 | 560.4 | 617.6 | 57200
| Assistant. Executive Engineer (Ele) | [6 empty] | Assistant Engineer (Ele)
| Nodal Centre-2, KPTCL | [6 empty] | 66/11kV MUSS, KPTCL
| Gowribidanur | [6 empty] | Chelur
Executive Engineer (Ele)
Operation Division KPTCL
Gowribidanur

## F10 & F3
F3. Stationwise High & Low Voltage Recorded during the month OF JANUARY - 2026
Bus Voltage in kV | Max. Voltage Recorded in kV | Date | Time ( HH:MM ) | Min. Voltage Recorded in kV | Date | Time ( HH:MM ) | Max. Demand in MW | Date | Time ( HH:MM )
66 kV | 67 | 2026-01-05 | 0.83333 | 61 | 2026-01-08 | 0.41667 | 10.8833 | 2026-01-24 | 0.375
11 kV ( BANK-1 ) | 11.6 | 2026-01-04 | 0.75 | 10.8 | 2026-01-20 | 0.41667
11 kV ( BANK-2 ) | 11.6 | 2026-01-09 | 0.41667 | 10.8 | 2026-01-20 | 0.41667
Ref. Bus Voltage in kV | No. of Incoming Feeders | No. of Outgoing Feeders | No. of Stepdown Transformer Bays | Net Stepdown Transformer Capacity in MVA | Net Energy Input in MU | Net Energy Output in MU
66 kV | 1 | 0 | 2 | 2X8 MVA | 2.322 | 0.4815
11 kV | 2 | 8 | 2

## Transformer tripping
Line/Transformer Tripping
66kV Incoming Line
Sl no | Date | From | To | Duration | Reason | Faulty
1 | [5 empty] | L/C
66kV outgoing Line Chakavelu
Sl no | Date | From | To | Duration | Reason | Faulty
20MW E.S.SUN POWER PVT LTD
Sl no | Date | From | To | Duration | Reason | Faulty
Transformer -1
Sl no | Date | From | To | Duration | Reason | Faulty
1 | 2026-01-05 | 13:20 | 13:30 | 0:10 | Transformer-1 tripped Directional OCR 'R'Phase & master trip relay 86 operated. Transformer overload. | L/T
2 | 2026-01-24 | 9:10 | 9:25 | 0:15 | Transformer-1 tripped on master trip relay 86 operated. | L/T
3 | 2026-01-24 | 9:40 | 11:10 | 1:30 | LC availed for bank-1, 11kv R phase CT red hot clamp replaced work . | L/C
Transformer -2
Sl no | Date | From | To | Duration | Reason | Faulty
1 | 2026-01-05 | 9:05 | 16:00 | 6:55 | LC availed for transformer-2 oil leakage arresting work as for work award.( work completed by the firm M/s cowda & co Hyderabad.) | L/C

## Station Losses
66/11 KV Chelur Sub-Station Losses for the month of JANUARY - 2026
| Station Losses | TC1-BANK-1 | BANK-1 TO Feeders | TC2-BANK-2 |  | BANK-2 TO Feeders
| 0.64% | 0.97% | 0.36% | 0.53% |  | 1.48
Assistant Engineer (Ele)
66/11kV MUSS, KPTCL
Chelur