## Peak load (hidden)
KARNATAKA POWER TRANSMISSION CORURATION LIMITED
66/11KV MUSS THYMAGONDLU
Peak load for the Month of Sept - 2015
Sl No. | Name of lines / Transformer | Maximum |  |  |  | Minimum load |  |  |  | Highest Voltage |  |  | Lowest Voltage
|  | Date | Time in hrs | MW | Amps | Date | Time in hrs | MW | Amps | Date | Time in hrs | KV | Date | Time in hrs | KV
1 | 66KV Dobaspet | 2 | 5:00 | 10.3 | 103 | 14 | 9:00 | 0.3 | 3 | 26 | 3:00 | 68 | 16 | 15:00 | 63
2 | T1-8MVA | 16 | 11:00 | 6.4 | 64 | 15 | 9:00 | 0.3 | 3 | 26 | 3:00 | 68 | 16 | 15:00 | 63
3 | T2-8MVA | 2 | 6:00 | 5.1 | 51 | 14 | 24:00 | 0.4 | 4 | 26 | 3:00 | 68 | 16 | 15:00 | 63
4 | BANK - I | 11 | 11:00 | 6.4 | 386 | 15 | 9:00 | 0.3 | 22 | 17 | 14:00 | 11.8 | 29 | 11:00 | 10.7
5 | F1-BIGBAG | 16 | 14:00 | 1.9 | 114 | 17 | 24:00 | 0.4 | 24 | 17 | 14:00 | 11.8 | 29 | 11:00 | 10.7
6 | F2-TRMN | 5 | 15:00 | 1.4 | 84 | 2 | 17:00 | 0.1 | 6 | 17 | 14:00 | 11.8 | 29 | 11:00 | 10.7
7 | F3-SATARAC | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
8 | F4- KALALGATTA | 3 | 12:00 | 1.2 | 72 | 28 | 5:00 | 0.06 | 4 | 17 | 14:00 | 11.8 | 29 | 11:00 | 10.7
9 | F9- Rama Hi-Power | 27 | 7:00 | 3.2 | 192 | 24 | 7:00 | 0.06 | 4 | 17 | 14:00 | 11.8 | 29 | 11:00 | 10.7
10 | F10- Doddabele | 17 | 20:00 | 0.4 | 24 | 17 | 17:00 | 0.1 | 6 | 17 | 14:00 | 11.8 | 29 | 11:00 | 10.7
11 | BANK -II | 2 | 6:00 | 5.1 | 310 | 14 | 24:00 | 0.4 | 24 | 17 | 14:00 | 11.8 | 21 | 16:00 | 10.6
12 | F5-Gundena Halli | 3 | 15:00 | 2.6 | 156 | 28 | 24:00 | 0.1 | 8 | 17 | 14:00 | 11.8 | 21 | 16:00 | 10.6
13 | F6-KSDL | 3 | 12:00 | 2.6 | 160 | 14 | 23:00 | 0.1 | 8 | 17 | 14:00 | 11.8 | 21 | 16:00 | 10.6
14 | F7-Beeragondanahalli | 16 | 14:00 | 1 | 60 | 28 | 23:00 | 0.06 | 4 | 17 | 14:00 | 11.8 | 21 | 16:00 | 10.6
15 | F8- Thotana Halli | 3 | 12:00 | 1.3 | 80 | 18 | 1:00 | 0.4 | 24 | 17 | 14:00 | 11.8 | 21 | 16:00 | 10.6
Assistant Engineer Elecl., 66/11KV MUSS KPTCL Thyamagondlu.

## EBC
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED.
66/11KV MUSS Hullenahalli
MONTH - March 2025
CONSOLIDATED MONTHLY METER READING DATA FOR STATIONS - FORMAT-1
Sl. No | Particulars Line/ Transformer/ Bank/ Feeder | CT Ratio Used / (Amps) | Energy Meter Sl No | Max Peak Load |  |  |  | Zone |  | BRAZ | Meter Constant in KWH. | Net Energy in MU | Meter Em or . | Status of meter, OK/MNR/NM | %Difference Line to Tr./Tr-to Tr/Tr to Bank/Bank to feeders | % error between Line to Tr./Tr to Bank/Bank to feeders
READINGS
|  |  |  | A | MW | Date | Time | Present | Previous | Difference
66kv Line. | [14 empty] | diff L-T | % err
1 | Anchepalya to Hullenahalli Line @ ANCHEPALYA END | 300/1 | 13190765 | 280 | 28 | 08.03.2025 | 22:00 | 20705.8 | 19917.7 | 788.1 | 18 | 14.1858 | SECURE | OK | Transmission loss Ancheplaya line | 2.4049
2 | ANCHEPALYA I/C LINE @Hullenahalli | 400/1 | KAU09259 | 286 | 28.6 | 2025-06-03 | 19:00 | 30101.64 | 29524.78 | 576.86 | 24000 | 13.8446 | SECURE | OK | Kudur line Loss | 0.46105 | 5.3422 | Kudur | PRESENT | PREIVOUS | DIFF | CONST | 3567600
3 | KUDUR LINE | 400/1 | Y0297996 | 245 | 24.5 | 2025-08-03 | 14:00 | 23926.1 | 22863.3 | 1062.8 | 8000 | 8.5024 | SECURE | OK | Station losses | 1.5334 | 5.2603 | TR1 | 1521.4 | 1224.1 | 297.3 | 12000 | 3567600
[18 empty] | TR2 | 30644.37 | 30432.57 | 211.8 | 12000 | 2541600
[12 empty] | 5.3422 | [5 empty] | OUTGOING | 29493 | 28316 | 1177 | 2000 | 2354000
1 | T1- 12.5 MVA | 200/1 | KAU09324 | 106 | 10.6 | 2025-01-03 | 8:00 | 50651.5 | 49809.7 | 841.8 | 3000 | 2.5254 | SECURE | OK | 0.01124 | 0.44508 | [5 empty] | TOTAL | 8.4632
2 | T2-20 MVA | 200/1 | 11070835 | 118 | 11.8 | 2025-08-03 | 10:00 | 131953.7 | 130549.9 | 1403.8 | 2000 | 2.8076 | L & T | OK | 0.06144 | 2.1883
5.333
11kV Readings. | [14 empty] | diff B1-F | % err
A | BANK - I | 800/1 | Q 0245701 | 599 | 9.9 | 2025-01-03 | 8:00 | 490.327 | 458.9 | 31.427 | 80000 | 2.5142 | SECURE | OK | 0.15626 | 6.2152
1 | F1-Neralekere | 200/1 | Q 0246043 | 140 | 2.3 | 2025-08-03 | 19:00 | 824.19 | 791.871 | 32.319 | 20000 | 0.64638 | SECURE | OK
2 | F2-Gangonahalli | 200/1 | Q 0245611 | 208 | 3.4 | 2025-02-03 | 18:00 | 1066.61 | 1040.673 | 25.937 | 20000 | 0.51874 | SECURE | OK
3 | F3-Tippasandra | 200/1 | Q 0245064 | 236 | 3.9 | 2025-01-03 | 8:00 | 826.47 | 802.349 | 24.121 | 20000 | 0.48242 | SECURE | OK
4 | F4-Hullenahalli | 200/1 | Q 0245630 | 232 | 3.8 | 2025-03-03 | 10:00 | 1095.64 | 1074.247 | 21.393 | 20000 | 0.42786 | SECURE | OK
5 | F10-Tavarekere | 200/1 | 16194002 | 88 | 1.4 | 2025-05-03 | 10:00 | 7218.6 | 6936.1 | 282.5 | 1000 | 0.2825 | L & T | OK
2.3579
B | BANK -II | 800/1 | Q 0245363 | 688 | 11.4 | 2025-08-03 | 21:00 | 1467.014 | 1432.687 | 34.327 | 80000 | 2.7462 | SECURE | OK | -0.13126 | -4.7798
6 | F5-Sankigatta | 200/1 | Q0245276 | 220 | 3.6 | 2025-05-03 | 16:00 | 389.079 | 364.661 | 24.418 | 20000 | 0.48836
7 | F6- Honnapura | 100/1 | Q 0245033 | 52 | 0.8 | 16/3/2025 | 9:00 | 154.607 | 122.349 | 32.258 | 10000 | 0.32258 | SECURE | OK
8 | F7 - Virupapura | 200/1 | Q0245368 | 188 | 3.1 | 2025-10-03 | 18:00 | 645.415 | 624.063 | 21.352 | 20000 | 0.42704
9 | F8 - Sugganahalli | 200/1 | Q 0245987 | 206 | 3.4 | 2025-03-03 | 13:00 | 606.771 | 582.994 | 23.777 | 20000 | 0.47554 | SECURE | OK
10 | F9-Hebalalu | 100/1 | Q 0245293 | 200 | 3.3 | 2025-10-03 | 17:00 | 568.767 | 549.992 | 18.775 | 20000 | 0.3755 | SECURE | OK
11 | F11- Beechanahalli | 200/1 | 16194004 | 220 | 3.6 | 2025-09-03 | 17:00 | 8438.6 | 8193.9 | 244.7 | 2000 | 0.4894 | L & T | OK
12 | F13-Chikkanahalli | 200-1 | 16194016 | 130 | 2.1 | 19/3/2025 | 17:00 | 11766.6 | 11617.1 | 149.5 | 2000 | 0.299 | L & T | OK
2.8774
11 | Station Auxiliary | 1 | 8820298 |  |  |  |  | 27275.4 | 27122.4 | 153 | 10 | 0.00153 | L & T | OK
Note : Augmentation of 8MVA by 20MVA Power Transformer commissioned on 01.03.2025 and load taken on 02.03.2025 at 19:53hrs, CT Ratio changed from 100/1 to 200/1A Also meter constant changed from 1000 to 2000. 2. Bank-2 feeder losses and Bank-1 feeder losses are more due to Bank-2 feeder feeding from Power Transformer-1 by bus coupler 01.03.2025 to 02.03.2025 upto 19:53hrs, 03.03.2025 from 09:45hrs to 12:25hrs for movement of crane(Dismantling of 8MVA Power Transformer -2 and 05.03.2025 from 12:45hrs to 14:00 for attending oil low alarm by ECE firm.
| Asst Executive Engineer (Ele) | [10 empty] | Asst Engineer (Ele)
| Nodal Nelamangala | [10 empty] | 66/11KV Hullenahalli SubStation

## BFORM
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
STATION B-FORMS OF IF POINTS
Name of the Station:66/11 kV S/S Hullenahalli | [9 empty] | IF Point Sl No.
Name of the TL & SS Division:Nelamangala | [9 empty] | Month: March 2025
SI NO | Sub-Station Names | Transformer Capacity and Make | Inter Face Points | Meter Serial No | CT Ratio | Flow Type | MF | IR | FR | Diff | Assed Consumption | Total Consumption
1 | Hullenahaali 66/11kV Sub Station | 12.5 MVA | Bank-1 | Q 0245701 | 800/1 | From KPTCL | 80000 | 458.9 | 490.327 | 31.427 |  | 2514160
To KPTCL
2 |  | 20 MVA | Bank-2 | Q0245363 | 800/1 | From KPTCL | 80000 | 1432.687 | 1467.014 | 34.327 |  | 2746160
[6 empty] | To KPTCL |  |  |  | 0
3 |  | 100kVA/ Vijay | Auxillary | 8820298 |  |  | 10 | 27122.4 | 27275.4 | 153 |  | 1530
HV Side Reading of Transformers
1 | Hullenahaali 66/11kV Sub Station | 12.5 MVA Andrew Yule | Transformer-1 | KAU 09304 | 200/1 | From KPTCL | 3000 | 49809.7 | 50651.5 | 841.8 |  | 2525400
To KPTCL
2 |  | 20 MVA Kanohar | Transformer-2 | KAU 09297 | 200/1 | From KPTCL | 2000 | 130549.9 | 131953.7 | 1403.8 |  | 2807600
To KPTCL
Note : Augmentation of 8MVA by 20MVA Power Transformer commissioned on 01.03.2025, CT Ratio changed from 100/1 to 200/1A Also meter constant changed from 1000 to 2000.
|  | Asst Executive Engineer (Ele) | [8 empty] | Asst Engineer (Ele)
|  | Nodal Officer, Operations Division Nelamangala | [7 empty] | 66/11KV Hullenahalli SubStation
Executive Engineer (Ele)
Operations Division,KPTCL Nelamangala

## IF Point comparison
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED.
66/11KV S.S Hullenahalli
MONTH :- March 2025
| 2025-02-28 | 2025-03-31
Name of Equipment | Energy | Energy | % Diff | Remarks
11kV Bank-1 | 3053600 | 2514160 | -21.4561 | Consumption in Feb is more due to During the month of Feb augmentation of 8MVA by 20MVA, All Bank-2 feeder feeding from Power Transformer-1
11kV Bank-2 | 1842720 | 2746160 | 49.0275 | Load increases due to low rain fall
Auxillary | 1299 | 1530 | 0.17783
Assistant Engineer Elecl., 66/11KV S/S KPTCL Hullenahalli.
Asst Executive Engineer (Ele) Nodal, Nelamangala

## Ancheplaya -Hullenahalli line
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Interruption of 66kV EHV Line from Anchepalya to Hullenahalli Muss for the month of March 2025
Sl. No. | Date | Interruption details | [6 empty] | Remarks
|  | Time of Tripping | Time of Charging | Duration | Unschedule | Schedule | Relay Acted | Reasons for Tripping
1 | 01.03.2025 | 8:17 | 8:27 | 0:10 |  | Yes |  | Line tripped on EFR-R phase distance 12.75 KM at 220KV Anchepalya
2 | 07.03.2025 | 13:50 | 13:57 | 0:07 |  | Yes |  | MSF to 220KV Anchepalya
3 | 08.03.2025 | 7:13 | 9:40 | 2:27 |  | Yes |  | Wave trap faulty at 220KV Anhepalya
| 08.03.2025 | 11:11 | 11:53 | 0:42 |  | Yes |  | MSF to 220KV Anchepalya
| Asst Executive Engineer (Ele) |  |  |  | Assistant Engineer Ele
| Nodal, Nelamangala |  |  |  | 66/11 KV MUSS Hullenahalli

## Hullenahalli-kudur line
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
INTERRUPTION OF 66kV EHV LINE OF 66/11kV Hullenahalli to Kudur MUSS for the Month of March 2025
Sl. No. | Date | Interruption details |  |  |  |  | Remarks
|  | Time of Tripping | Time of Charging | Duration | Relay Acted | Reasons for Tripping
1 | Nil
|  | Asst Executive Engineer (Ele) |  |  |  | Assistant Engineer Ele
|  | Nodal, Nelamangala |  |  |  | 66/11 KV MUSS Hullenahalli

## Power Transformer
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Power Transformer Interruption of March 2025 of 66/11kV S.S Hullenahalli
Line / ICT Ref. | Line Name | Scheduled & Unscheduled Interruptions Details |  |  |  | Scheduled | Un Scheduled | Remarks
|  | Date | From | To | Total Hrs |  |  | Relay indications | Fault Analysis
|  | Date | Time | Time
| Anchepalya Solur line | 2015-09-22 | 11.25 | 11.44 | 0.19 | _ | Tripped on Dist Relay, Dist-16.8KM,Dist L1E on,Dir O/C 'R' Ph P/U,Z1 trip,IL1=1.26KA IL2=0.14KA,IL3=0.12KA at Dobaspet. | _ | Temporary fault
|  | 2015-09-23 | 11.25 | 12.13 | 0.48 | _ | 220KV Nelamangala & Kadur Line Tripped on Fault at Dobaspet. | _ | L/F
|  | 2015-09-23 | 21.15 | 22.24 | 1.09 | _ | Tripped on Dist Relay, Dist-6.2KM, R & Y Phase P/U, Dir O/C 'R'&'Y' Phase P/U,IL1-2.68KA, IL2-2.07KA, IL3-0.14KA Zone-1 trip at Dobaspet. | _ | L/F
|  | 2015-09-26 | 10.14 | 10.24 | 0.1 | _ | Tripped on Dist Relay ,Dist-11KM, Z1 Trip, R & Y Phas P/U, Dir O/C 'Y' Phase P/U,IL1-2.68KA,IL2-2.07KA,IL3-0.14KA Dist L1-E & L2-E Dist 3P ON at Dobaspet. | _ | L/F
|  | 2015-09-28 | 19.09 | 19.29 | 0.2 | Tripped for L/S as per the LDC Instruction due to load restriction at Dobaspet. | _ | _ | L/S
66 KV Transformers | 12.5 MVA TR-1 | Nil
| 20MVA TR-2 | 01.03.2025 | 0:00 | 16:40 | 16:40 | YES |  |  | LC availed for augmentation of 8MVA by 20MVA Power Transformer
|  | 02.03.2025 | 16:45 | 19:50 | 3:05 | YES |  |  | LC availed for SFRA test by Firm
|  | 03.03.2025 | 9:45 | 12:25 | 2:40 | YES |  |  | LC availed of crane for dismantling of 8MVA Power Transformer-2
|  | 05.03.2025 | 12:45 | 14:00 | 1:15 | YES |  |  | LC availed for oil level low aram attending by ECE firm
|  | 23.03.2025 | 13:15 | 13:50 | 0:35 | YES |  |  | LC availed for oil level low aram attending by ECE firm
| Asst Executive Engineer (Ele) | [6 empty] | Assistant Engineer Ele
|  | Nodal, Nelamangala | [5 empty] | 66/11 KV MUSS Hullenahalli
;

## Voltage
Maximum and Minimum Voltages
Month: March 2025
SL No | Division | Name of the stations | Voltage class | HV SIDE | [5 empty] | LV SIDE BANK1 | [5 empty] | LV SIDE BANK2
|  |  |  | Max. Voltage in KV | Date | Time | Min. Voltage in KV | Date | Time | Max. Voltage in KV | Date | Time | Min. Voltage in KV | Date | Time | Max. Voltage in KV | Date | Time | Min. Voltage in KV | Date | Time
1 | Nelamangala | Hullenahalli | 66KV | 66 | 01.03.2025 | 17:00 | 60 | 06.03.2025 | 22:00 | 11.5 | 18.03.2025 | 21:00 | 10.7 | 01.03.2025 | 8:00 | 11.5 | 17.03.2025 | 12:00 | 10.6 | 03.03.2025 | 13:00
|  | Asst Executive Engineer (Ele) | [6 empty] | Assistant Engineer(Ele)
|  | Nodal, Nelamangala | [6 empty] | 66/11KV Substation,KPTCL
Hullenahalli

## Station consumption format
Total consumption & Peak load of 66kV sub stations pertaining to Bengaluru Zone as on March-2025
slno | Circle | TL & SS Division | Name of sub station | Voltage class in kV | 66kV side Transformer capacity in MVA | Total MVA of 66kV | Total station consumption March-2024 (Mu) | Max peak load (other than contingency peak) recorded during March - 2024 (MW) | Peak Load Time in HH:MM | Peak Load Date in DD/MM/YYYY | % loading | Load shedding(Trf /line over loading/SLDC inst.) | Action plan/Remedial Measures
8 | RMG | NMG | Hullenahalli | 66/11 | 1X8 , 1X12.5 | 20.5 | 5.333 | 22.4 | 8:00 |  | 161.9% |  | 1)66kV link Line between Gudemarahalli to Kudur substation is approved in APW 2018-19. 2)DPR is approved for Replacing 2x8MVA, 66/11kV Power Transformer by 1x12.5 and 1X20MVA-20MVA Power Transformer to be allotted | 13.8375

## Feeder details
| Details of existing feeders in Bengaluru Zone as on March-2024 | [10 empty] | Feeder added details if any
Dvn slno | Sl. no | Circle | TL & SS Division | Name of sub station | Voltage class in kV | Transformer capacity in MVA | Total MVA | DOC | No. of 11kV feerders | No. of idle 11kV feerders | Feeder no. | Feeder name | Feeder type | Feeder commissioned date
9 | 119 | RMG | NMG | Hullenahalli | 66/11 | 1X12.5, 1X8MVA | 20.5 | 2008-12-31 | 12 | 0

## Energy format
2025-03-31
S.No | Zone | Station name | Bank No | Feeders in that bank | Feeder/Bank Metering Status (Metered/ unmetered) | Feeder/Bank Metering Status (AMI/AMR) or Others(Specify if Others) | Status of Meter (Functional/Non-functional) | Metering Date | Feeder Type (Agri/ Industrial/Mixed) | Status of Communication | [9 empty] | Remarks (Source of data)
[8 empty] | Date of last actual meter reading/ communication |  | % data received through automatically if feeder AMR/AMI | Number of hours when meter was unable to communicate in period | Total Number of hours in the period | Meter Make | Meter SL.No | CT/PT ratio | IR | FR | Meter Constant | Total Input Energy
8 | Bangalore | 66/11KV Hullenahalli | Bank -1 | Bank -1 | Metered |  | Functional | 31.03.2025 |  |  |  |  | Secure | Q 0245701 | 800/1 | 458.9 | 490.327 | 80000 | 2.5142
| Bangalore |  |  | F1-Neralekere | Metered |  | Functional | 31.03.2025 | NJY |  |  |  | Secure | Q 0246043 | 200/1 | 791.871 | 824.19 | 20000 | 0.64638
| Bangalore |  |  | F2 - Gangonahalli | Metered |  | Functional | 31.03.2025 | Agri |  |  |  | Secure | Q 0245611 | 200/1 | 1040.673 | 1066.61 | 20000 | 0.51874
| Bangalore |  |  | F3-Tippasandra | Metered |  | Functional | 31.03.2025 | Agri |  |  |  | Secure | Q 0245064 | 200/1 | 802.349 | 826.47 | 20000 | 0.48242
| Bangalore |  |  | F4 - Hullenahalli | Metered |  | Functional | 31.03.2025 | Agri |  |  |  | Secure | Q 0245630 | 200/1 | 1074.247 | 1095.64 | 20000 | 0.42786
| Bangalore |  |  | F10-Taverekere | Metered |  | Functional | 31.03.2025 | NJY |  |  |  | L&T | 16194002 | 200/1 | 6936.1 | 7218.6 | 1000 | 0.2825
| Bangalore |  | Bank-2 | Bank-2 | Metered |  | Functional | 31.03.2025 |  |  |  |  | Secure | Q 0245363 | 800/1 | 1432.687 | 1467.014 | 80000 | 2.7462
|  |  |  | F5-Sankigatta | Metered |  | Functional | 31.03.2025 | Agri |  |  |  | Secure | Q0245368 | 200/1 | 364.661 | 389.079 | 20000 | 0.48836
| Bangalore |  |  | F6-Honnapura | Metered |  | Functional | 31.03.2025 | NJY |  |  |  | Secure | Q 0245033 | 100/1 | 122.349 | 154.607 | 10000 | 0.32258
|  |  |  | F7-Virupapura | Metered |  | Functional | 31.03.2025 | Agri |  |  |  | L&T | 16194016 | 200-1 | 624.063 | 645.415 | 2000 | 0.042704
| Bangalore |  |  | F8-Sugganahalli | Metered |  | Functional | 31.03.2025 | Agri |  |  |  | Secure | Q 0245987 | 200/1 | 582.994 | 606.771 | 20000 | 0.47554
| Bangalore |  |  | F9-Hebbalalu | Metered |  | Functional | 31.03.2025 | NJY |  |  |  | Secure | Q 0245293 | 200/1 | 549.992 | 568.767 | 20000 | 0.3755
| Bangalore |  |  | F11- Beechanahalli | Metered |  | Functional | 31.03.2025 | Agri |  |  |  | L&T | 16194004 | 200/1 | 8193.9 | 8438.6 | 2000 | 0.4894
| Bangalore |  |  | F13-Bechanahalli | Metered |  | Functional | 31.03.2025 | Agri |  |  |  | Secure | Q0245276 | 200/1 | 4.723 | 5.23 | 20000 | 0.01014

## BESCOM KPTCL Interruption
NELAMANGALA DIVISION PEAK LOAD & INTERRUPTIONS OF 11kV FEEDERS FOR THE MONTH OF March 2025
SL NO | CIRCLE | DIVISION NAME | STATION NAME_SCADA | 11kV FEEDERS ACTUAL | CATEGORY | BESCOM SUB DIVISION & O&M UNIT COVERED | Schedule Interruption |  |  |  | Un-schedule Interruption |  |  |  | Remarks if any changes in 11kV Feeders to be highlightnened | Peak load of month
[7 empty] | KPTCL PART |  | BESCOM PART |  | KPTCL PART |  | BESCOM PART
[7 empty] | Nos. | Duration | Nos. | Duration | Nos. | Duration | Nos. | Duration |  | Peak Load in MW | Date | Time
89 | RAMANAGARA | Nelamangala | HULLENAHALLI_66 | F1-NERALEKERE | NJY | Kudur Subdivision Thipasandra O&M | 2 | 1:20 | 50 | 39:43 | 4 | 3:27 | 40 | 27:25 |  | 2.3 | 45872 | 19:00
90 | RAMANAGARA | Nelamangala | HULLENAHALLI_66 | F2-GANGONAHALLI | RURAL | Kudur Subdivision Thipasandra O&M | 0 | 0:00 | 8 | 5:40 | 1 | 0:07 | 18 | 23:02 |  | 3.4 | 45691 | 18:00
91 | RAMANAGARA | Nelamangala | HULLENAHALLI_66 | F3-TIPPASANDRA | RURAL | Kudur Subdivision Thipasandra O&M | 0 | 0:00 | 15 | 8:01 | 2 | 3:10 | 36 | 65:50 |  | 3.9 | 45660 | 8:00
92 | RAMANAGARA | Nelamangala | HULLENAHALLI_66 | F4-HULLENAHALLI | RURAL | Kudur Subdivision Thipasandra O&M | 1 | 0:35 | 24 | 12:30 | 3 | 3:20 | 26 | 47:08 |  | 3.8 | 45719 | 10:00
93 | RAMANAGARA | Nelamangala | HULLENAHALLI_66 | F5-SANKIGATTA | RURAL | Kudur Subdivision Thipasandra O&M | 0 | 0:00 | 16 | 10:43 | 2 | 3:10 | 23 | 57:40 |  | 3.6 | 45780 | 16:00
94 | RAMANAGARA | Nelamangala | HULLENAHALLI_66 | F6-HONNAPURA | NJY | Kudur Subdivision Thipasandra O&M | 2 | 1:10 | 38 | 32:17 | 4 | 3:27 | 16 | 18:20 |  | 0.8 | 16/3/2025 | 9:00
95 | RAMANAGARA | Nelamangala | HULLENAHALLI_66 | F7-VIRUPAPURA | RURAL | Kudur Subdivision Thipasandra O&M | 2 | 1:10 | 6 | 6:15 | 2 | 3:10 | 25 | 51:20 |  | 3.1 | 45933 | 18:00
96 | RAMANAGARA | Nelamangala | HULLENAHALLI_66 | F8-SUGGANAHALLI | RURAL | Kudur Subdivision Thipasandra O&M | 1 | 0:35 | 8 | 5:57 | 1 | 0:07 | 18 | 43:00 |  | 3.4 | 45719 | 13:00
97 | RAMANAGARA | Nelamangala | HULLENAHALLI_66 | F9-HEBBALALU | NJY | Kudur Subdivision Thipasandra O&M | 1 | 0:35 | 10 | 9:40 | 5 | 1:17 | 14 | 26:15 |  | 3.3 | 45933 | 17:00
98 | RAMANAGARA | Nelamangala | HULLENAHALLI_66 | F10-TAVAREKERE | NJY | Kudur Subdivision Thipasandra O&M | 2 | 1:20 | 21 | 21:07 | 4 | 3:27 | 20 | 20:25 |  | 1.4 | 45780 | 10:00
99 | RAMANAGARA | Nelamangala | HULLENAHALLI_66 | F11-BEECHANAHALLI | RURAL | Kudur Subdivision Thipasandra O&M | 0 | 0:00 | 10 | 6:05 | 1 | 0:10 | 41 | 58:55 |  | 3.6 | 45903 | 17:00
100 | RAMANAGARA | Nelamangala | HULLENAHALLI_66 | F13-Chikkahalli | RURAL | Kudur Subdivision Thipasandra O&M | 1 | 0:35 | 8 | 5:52 | 2 | 3:10 | 23 | 36:27 |  | 2.1 | 19/3/2025 | 17:00
| Asst Executive Engineer (Ele) | [10 empty] | Asst Engineer (Ele)
| Nodal Nelamangala | [10 empty] | 66/11KV Hullenahalli SubStation