## c19
MONTH: | [5 empty] | 2025-08-01
CONSOLIDATE MONTHLY METER READING DATA FOR STATIONS - FORMAT-1
Sl. No | Particulars Line/ Transformer/ Bank/ Feeder | CT Ratio Used / (Amps) | Energy Meter Sl No | Peak Load |  |  | Zone |  |  | BMAZ | Meter Constant in KWH. | Net Energy in KWH | Meter Em or ETV. Make | Status of meter, OK/MNR/NM | Remarks | Mw in Munits
[7 empty] | Imp/Exp | READINGS
|  |  |  | MW | Date | Time |  | Present | Previous | Difference
Name of the Station: 66/11 KV MUSS Army Welfare Housing Organisation Station Code: 1110124 | [10 empty] | AE(M) - 9480812586 No.18
1 | Incoming Line from Kadugodi | 400/1 | 13192708 | 31.4 | 02.08.2025 | 9:00 | Imp | 819682 | 809404 | 10278 | 2000 | 20556000 | L & T ETV | OK |  | 20.556
|  |  |  | 0 | 0 | 0:00 | Exp | 1287 | 1287 | 0 | 2000 | 0 |  |  |  | 0
2 | 66KV Konadasapura Line ( GIS) | 400/1 | 22005470 | 7.5 | 24.08.2025 | 15:00 | Imp | 5.309 | 5.29 | 0.019 | 480000 | 9120 | L & T ETV | OK |  | 0.00912
|  |  |  | 0 | 0 | 0:00 | Exp | 0.143 | 0.143 | 0 | 480000 | 0 |  |  |  | 0
3 | 66KV NTT O/G Line (GIS) | 400/1 | 22001475 | 14.4 | 25.08.2025 | 15:00 | Exp | 541.721 | 517.973 | 23.748 | 480000 | 11399040 | L & T ETV | OK |  | 11.399 | stn consn
|  |  |  | 0 | 0 | 0:00 | Imp | 0.065 | 0.065 | 0 | 480000 | 0 |  |  |  | 0 | 20556000
[10 empty] | 0 |  | 0
| 66/11 KV Transformers | [8 empty] | 0 |  | 0
1 | T 1-20MVA:66kv Side(HV) | 200/1 | 13192682 | 0 | 0 | 0:00 | Exp | 164239 | 164239 | 0 | 1000 | 0 | L & T ETV | OK |  | 0 | TR1 | #DIV/0!
2 | T 2-31.5MVA:66kv Side(HV) | 400/1 | 18152942 | 17.9 | 02.08.2025 | 9:00 | Exp | 1282.14 | 1243.92 | 38.22 | 240000 | 9172800 |  | OK |  | 9.1728 | TR-2 | 0.53201
| 11 KV Readings | [8 empty] | 0 |  | 0
| BANK I | 1200/1 | Q0247003 | 0 | 0 | 0:00 | Imp | 899.917 | 899.917 | 0 | 120000 | 0 | DLMS | OK |  | 0 | B1 | #REF!
1 | F-1 DP-5:H Block | 400/1 | Q0251114 | 0.12 | 08.08.2025 | 8:00 | Exp | 1.894 | 0.291 | 1.603 | 40000 | 64120 | DLMS | OK |  | 0.06412
2 | F-2 DP-4 Koraluru | 400/1 | Q0247269 | 4 | 03.08.2025 | 9:00 | Exp | 2391.918 | 2353.8 | 38.118 | 40000 | 1524720 | DLMS | OK |  | 1.5247 | BA2 | 0.14815
3 | F-3 DP-3:E,D Block | 400/1 | Q0246442 | 0.34 | 08.08.2025 | 9:00 | Exp | 274.703 | 269.712 | 4.991 | 40000 | 199640 | DLMS | OK |  | 0.19964
4 | F-4 DP-2:G,C Block | 400/1 | Q0247252 | 0.28 | 08.08.2025 | 8:00 | Exp | 209.445 | 206.145 | 3.3 | 40000 | 132000 | DLMS | OK |  | 0.132
5 | F-5 DP-1: A,B Block | 400/1 | Q0246749 | 0.22 | 18.08.2025 | 8:00 | Exp | 168.31 | 165.548 | 2.762 | 40000 | 110480 | DLMS | OK |  | 0.11048
6 | F-6 Station Auxiliary | 400/1 | Q0247233 | 0.01 | 01.08.2025 | 8:00 | Exp | 3.484 | 3.399 | 0.085 | 40000 | 3400 | DLMS | OK |  | 0.0034
7 | F-7 Capacitor Bank | [8 empty] | 0 |  | 0 |  |  |  | 0
8 | F-8 V-GIRI | 200/1 | 17094107 | 0.4 | 04.08.2025 | 8:00 | Exp | 9750.3 | 9606.5 | 143.8 | 1000 | 143800 | L & T ETV | OK |  | 0.1438
9 | F-10 Assetz Marq | 400/1 | 19005591 | 0.7 | 06.08.2025 | 7:00 | Exp | 8401.8 | 8230.6 | 171.2 | 2000 | 342400 | L & T ETV | OK | CT Ratio changed from 200 to 400 on 13.08.2024 | 0.3424
[10 empty] | 0 | [5 empty] | 0
| BANK 2 | 2000/1 | 17167052 | 17.2 | 02.08.2025 | 9:00 | Imp | 300725 | 292006 | 8719 | 1000 | 8719000 | L & T ETV | OK |  | 8.719
10 | F-9 C-GIRI | 200/1 | KA908126 | 1.7 | 31.08.2025 | 9:00 | Exp | 26188.9 | 25755.9 | 433 | 2000 | 866000 | Secure Meters | OK | CT Ratio changed from 200 to 400 on 25.11.2024 | 0.866
11 | F-11 Whitefield Ganesha Temple | 400/1 | 19009741 | 1.1 | 11.08.2025 | 9:00 | Exp | 13976.1 | 13746.8 | 229.3 | 2000 | 458600 | L & T ETV | OK |  | 0.4586
12 | F-12-Sadaramangala | 400/1 | 19009797 | 2.2 | 07.08.2025 | 7:00 | Exp | 21777.5 | 21584.9 | 192.6 | 2000 | 385200 | L & T ETV | OK |  | 0.3852
13 | F-13-Seegehalli | 400/1 | 19009766 | 5.1 | 03.08.2025 | 9:00 | Exp | 52484 | 51085.1 | 1398.9 | 2000 | 2797800 | L & T ETV | OK |  | 2.7978
14 | F-14 Sai Garden* | 400/1 | 19009755 | 5 | 22.08.2025 | 19:00 | Exp | 41526.8 | 40687.6 | 839.2 | 2000 | 1678400 | L & T ETV | OK |  | 1.6784
15 | BANK-2A | 1200/1 | 21001401 | 0.7 | 05.08.2025 | 7:00 | Imp | 12850 | 12445 | 405 | 1000 | 405000 | L & T ETV | OK |  | 0.405
16 | F-15 Sumadhura | 200/1 | 21001818 | 0.7 | 05.08.2025 | 7:00 | Exp | 12830.4 | 12426 | 404.4 | 1000 | 404400 | L & T ETV | OK |  | 0.4044
0
17 | STATION AUXILLARY | [8 empty] | Bank Total | 9128940
| Station Auxillary LV Side | 50/5 | 12043305 |  |  |  |  | 32090.43 | 31713.41 | 377.02 | 10 | 3770.2 | L & T ETV | OK
0
% OF ERROR :- (Transformer1-Bank1) /Transformer1)*100 = | [9 empty] | #DIV/0!
% OF ERROR :- (Transformer2-Bank2) /Transformer2)*100 = | [9 empty] | 0.532% | [6 empty] | Banks Total
NOTE: 20MVA TR-1 (SPEC) Released and Dismantling done on 29.05.2024 @ 11:35 hrs and shifted to B station.

## cf7
KARNATAKA POWER TRANSMISSION CORPORATION LTD.
MONTH: -AUG-2025
CONSUMPTION OF 11KV FEEDERS IN HOODY TL & SS DIVISION
Sl No | Name of the Station | Sl No | Name of the Feeders | Category U/R | Feeders Comsumption in KWH | Consumption at I.F Points in KWH | Intruption during the month in Hours | [7 empty] | Remarks
[7 empty] | Line Clear |  | Load Shedding |  | Single phase |  | Faulty
[7 empty] | Nos | Dur | Nos | Dur | Nos | Dur | Nos | Dur
1 | 66/11 KV Army Welfare Housing Organisation |  | BANK I |  |  | 0 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0
2 |  |  | BANK 2 |  |  | 8719000 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0
3 |  |  | BANK2A |  |  | 405000 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0
4 |  | 1 | F-1 DP-5 | U | 64120 |  | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0
5 |  | 2 | F-2 DP-4 Koraluru | U | 1524720 |  | 19 | 9:49 | 0 | 0:00 | 0 | 0:00 | 60 | 0.75972
6 |  | 3 | F-3 DP-3 | U | 199640 |  | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0
7 |  | 4 | F-4 DP-2 | U | 132000 |  | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0
8 |  | 5 | F-5 DP-1 | U | 110480 |  | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0
9 |  | 6 | F-6 Station Auxiliary | U | 3400 |  | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0
10 |  | 7 | F-7 Capacitor Bank | U | 0 |  | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0
11 |  | 8 | F-8 V-GIRI | U | 143800 |  | 1 | 0:31 | 0 | 0:00 | 0 | 0:00 | 4 | 0.56806
12 |  | 9 | F-9 C-GIRI | U | 866000 |  | 8 | 2:52 | 0 | 0:00 | 0 | 0:00 | 18 | 0.23889
13 |  | 10 | F-10 Assetz | U | 342400 |  | 0 | 0:00 | 0 | 0:00 | 0 | 0 | 0 | 0
14 |  | 11 | F-11 Whitefield Ganesha Temple | U | 458600 |  | 1 | 8:54 | 0 | 0:00 | 0 | 0 | 6 | 0.23333
15 |  | 12 | F-12-Sadaramangala | U | 385200 |  | 9 | 172:25 | 0 | 0:00 | 0 | 0 | 8 | 1900-01-02 16:42
16 |  | 13 | F-13 Seegehalli | U | 2797800 |  | 15 | 4:32 | 1 | 1:00 | 0 | 0 | 20 | 0.21528
17 |  | 14 | F-14 Sai Garden | U | 1678400 |  | 10 | 3:27 | 0 | 0:00 | 0 | 0 | 15 | 0.25347
18 |  | 15 | F-15 Sumadhura | U | 404400 |  | 0 | 0:00 | 0 | 0:00 | 0 | 0 | 0 | 0
TOTAL |  |  |  |  | 9110960 | 9124000

## 11kV Bank & Feeder Intpn.
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED.
MONTH:-AUG-2025
.
Sl No | Name of the Station | Sl No | Name of the feeders | EFR |  | OCR |  | EFR & OCR |  | Major Break Downs |  | Unscheduled |  |  |  | Hand Trip |  | Line Clear |  | Load Shedding |  | Scheduled |  | Remarks
|  |  |  | Nos | Dur | Nos | Dur | Nos | Dur | Nos | Dur | Nos | 0.5 | Nos. | >0.5 | Nos | Dur | Nos | Dur | Nos | Dur | Nos | Dur |  | FAULTY
1 | 66/11kv Army Welfare housing organisation |  | BANK 1 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0:00 | 0 | 0:00
|  |  | BANK 2 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0:00 | 0 | 0:00
|  |  | BANK-2A | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0:00 | 0 | 0:00
|  | 1 | F-1 DP-5 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0:00 | 0 | 0:00
|  | 2 | F-2 DP-4 Koraluru | 47 | 11:23 | 11 | 5:49 | 2 | 1:02 | 0 | 0:00 | 0 | 0:00 | 60 | 18:14 | 0 | 0:00 | 19 | 9:49 | 0 | 0:00 | 19 | 9:49 |  | 60 | 18:14 | 19 | 9:49
|  | 3 | F-3 DP-3 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0:00 | 0 | 0:00
|  | 4 | F-4 DP-2 | 0 | 0:00 | 0 | 0:00 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0:00 | 0 | 0:00
|  | 5 | F-5 DP-1 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0:00 | 0 | 0:00
|  | 6 | F-6 Station Auxiliary | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0:00 | 0 | 0:00
|  | 7 | F-7 Capacitor Bank | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 00:00 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0:00 | 0 | 0:00
|  | 8 | F-8 V-GIRI | 0 | 0:00 | 1 | 0:04 | 3 | 13:34 | 0 | 0:00 | 0 | 0:00 | 4 | 13:38 | 0 | 0:00 | 1 | 0:31 | 0 | 0:00 | 1 | 0:31 |  | 4 | 13:38 | 1 | 0:31
|  | 9 | F-9 C-GIRI | 13 | 3:18 | 1 | 0:26 | 4 | 2:00 | 0 | 0:00 | 0 | 0:00 | 18 | 5:44 | 0 | 0:00 | 8 | 2:52 | 0 | 0:00 | 8 | 2:52 |  | 18 | 5:44 | 8 | 2:52
|  | 10 | F-10 Assetz | 0 | 0:00 | 0 | 0:00 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0 | 0 | 0:00
|  | 11 | F-11 Whitefield Ganesha Temple | 6 | 5:36 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 6 | 5:36 | 0 | 0:00 | 1 | 8:54 | 0 | 0:00 | 1 | 8:54 |  | 6 | 5:36 | 1 | 8:54
|  | 12 | F-12 Sadaramangala | 0 | 0:00 | 0 | 0:00 | 8 | 88:42 | 0 | 0:00 | 0 | 0:00 | 8 | 88:42 | 0 | 0:00 | 9 | 172:25 | 0 | 0:00 | 9 | 172:25 |  | 8 | 88:42 | 9 | 172:25
|  | 13 | F13- Seegehalli | 15 | 3:37 | 1 | 0:15 | 4 | 1:18 | 0 | 0:00 | 0 | 0:00 | 20 | 5:10 | 0 | 0:00 | 15 | 4:32 | 1 | 1:00 | 16 | 5:32 |  | 20 | 5:10 | 16 | 5:32
|  | 14 | F-14 Sai Garden | 5 | 1:16 | 2 | 0:29 | 8 | 4:20 | 0 | 0:00 | 0 | 0:00 | 15 | 6:05 | 0 | 0:00 | 10 | 3:27 | 0 | 0:00 | 10 | 3:27 |  | 15 | 6:05 | 10 | 3:27
|  | 15 | F-15 Sumadhura | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0:00 | 0 | 0:00
0

## Tr.Peak load
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
(Cons) PEAKLOAD DETAILS PERTAINS TO HOODY DIVISION. MONTH:-AUG-2025
Sl No | Name of the Station. | Transformer Ratio in KV. | Transformer Capacity in MVA. | Total MVA. | Peak Load in MW. | Peak Load in Amps. Primary-Side. | Date. | Time | Percentage of Loading.
1 | 66/11 KV Army Welfare Housing Organisation | TR:1:-66 / 11 | 20 MVA | 51.5 | 0 | 0 | 0 | 0:00 | 0%
2 |  | TR:2:-66 / 11 | 31.5MVA |  | 17.9 | 179 | 02.08.2025 | 9:00 | 64.97%

## Lines peak
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED.
MONTH:AUG-2025
(CONS) FORMAT 2 (Pertains to Hoody TL & SS Division).
Sl No | Name of the Station | Name of the Lines | Maximum peak load |  |  |  |  | No. of Interruptions |  |  |  | Energy Sent out in KWH
|  |  | Recorded during the month |  |  |  |  | Forseen |  | Unforseen
|  |  | MW | Amps | Date | Time | MVAR | Nos | Hrs | Nos | Hrs | Import | Export
| 66/11 KV Army Welfare Housing Organisation | 66KV Incoming Line from 66KV Kadugodi MUSS (Line 2) | 31.4 | 314 | 02.08.2025 | 9:00 |  | 0 | 0:00 | 0 | 0:15 | 20556000 | 0
1 |  | 66KV Konadaspura MUSS(GIS) | 7.5 | 75 | 24.08.2025 | 15:00 |  | 1 | 0:05 | 0 | 0:00 | 9120 | 0
|  | 66KV Out Going NTT (GIS) Line | 14.4 | 144 | 25.08.2025 | 15:00 |  | 0 | 0:00 | 1 | 2:05 | 0 | 11399040
0

## Stn. Peak
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED.
MONTH: AUG-2025
(CONS) FORMAT 1 (Pertains to Hoody TL & SS Division)
Sl No | Name of the station | Tr. In MVA | Max Peak Load Recorded |  |  |  |  | Max Voltage Recorded in KV | [5 empty] | Min Voltage Recorded in KV | [5 empty] | Received from I.P.P.S |  | Energy sent out from MUSS in KWH |  | Max peak load (other than contingency peak) recorded (MW) | Total station consumption (mu) | Date & Time DD/MMM/YY_HH;MM
|  |  | MW | Amps | Date | Time In Hrs | MVAR | HV/KV | Date | Time In Hrs | LV/ KV | Date | Time In Hrs | HV/KV | Date | Time In Hrs | LV/ KV | Date | Time In Hrs | 11KV (Max) | EHV (Min) |  |  | 17.9 | 9.124 | 02.08.2025 @ 09:00
1 | 66/11 KV Army Welfare Housing Organisation | 31.5 | 17.9 | 1074 | 02.08.2025 | 9:00 |  | 67 | 01.08.2025 | 1:00 | 11.1 | 01.08.2025 | 1:00 | 64 | 01.08.2025 | 7:00 | 10.7 | 01.08.2025 | 7:00 |  |  | 9124000
02.08.2025
09:00
[24 empty] | max | max | min | min
[23 empty] | hv | 01.08.2025 | 01:00 | 01.08.2025 | 01.08.2025
[23 empty] | lv | 01.08.2025 | 01:00 | 01.08.2025 | 07:00
[23 empty] | 67 | 01.08.2025 @ 01:00 | 64 | 01.08.2025 @ 01:00 | 11.1 | 01.08.2025 @ 01:00 | 10.7 | 01.08.2025 @ 07:00 | -

## R-Index
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED.
MONTH:-AUG-2025
RELIABILITY INDEX
SL. NO. | Name of the Station | voltage class | T | N | T-N | Reliability T-N / T X 100 | Remarks
1 | 66/11 KV Army Welfare Housing Organisation | 66/11kV | 744:00 | 0:15 | 743:45 | 99.97%
Note:- T=Total No. of Hours in the month.
N- Unscheduled interruptions (shut down hours of the station) during the month due to failure of major equipments, such as transformers, breakers, 66KV jumps, pot head, (66KV & 11KV) Bank, feeder & switchgear troubles.

## B forms
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
B-Forms of IF Points
Name of the Station: Army Welfare Housing Organisation | [8 empty] | IF point Sl No:
Name of the Division: TL-SS Division Hoody | [8 empty] | Month: | 2025-08-01
Sl. No. | Sub-Station Name | Interface Point | Meter Type | CT Ratio | Meter SL No. | Flow Type | MF | Final | Initial | Consumption | Remarks
1 | Army Welfare Housing Organisation | BANK-1 | Secure ETV | 1200/1 | Q0247003 | Import | 120000 | 899.917 | 899.917 | 0
2 |  | BANK-2 | L & T ETV | 1200/1 | 17167052 | Import | 1000 | 300725 | 292006 | 8719000
3 |  | BANK 2A | L & T ETV | 1200/1 | 21001401 | Import | 1000 | 12850 | 12445 | 405000
4 |  | AUX | L & T ETV | 50/5 | 12043305 | Export | 10 | 32090.43 | 31713.41 | 3770.2 |  | -22.5
5 |  | EHT | --- | --- | --- | --- | --- | --- | --- | ---
Annexure
Sl. No. | Sub-Station Name | Interface Point | Meter Type | CT Ratio | Meter SL No. | Flow Type | MF | Final | Initial | Consumption | Remarks | -2702280
1 | Army Welfare Housing Organisation | Transformer-1 | L&T ETV | 200/1 | 13192682 | Export | 1000 | 164239 | 164239 | 0
2 |  | Transformer-2 | L&T ETV | 400/1 | 18152942 | Export | 240000 | 1282.14 | 1243.92 | 9172800
Assessed consumption (1% Transformer losses)
Transformer HV reading - 1 % Transformer loss = IF point consumption
Assistant Engineer (Elec.), |  |  | Assistant Executive Engineer (Elec.), |  |  | Assistant Executive Engineer (Elec.), |  |  |  | Executive Engineer (Ele)
66/11 kV AWHO MUSS |  |  | HRMSD-2,Hoody,KPTCL. |  |  | O&M Sub-division, BESCOM |  |  |  | Operation Division, Hoody,KPTCL.

## 66KV Interruption Scheduled
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
MONTH:-JULY-2025
Sl.No. | Name of the line | Date | From | To | Duration | Reason
1 | I/C LINE-2 KADUGODI | 24.08.2025 | 13:40 | 13:55 | 0:15 | INCOMING SUPPLY FAILURE FROM KADUGODI STATION DUE TO I/C FAILURE FROM EPIP 22KV END AND LOAD CHANGEOVER TO KONADASAPURA
2 | I/C LINE-1 KONADASAPURA | 24.08.2025 | 15:50 | 15:55 | 0:05 | 66KV KONADASAPURA LINE H/T TAKEN FOR LOAD CHANGEOVER TO KADUGODI LINE
3 | O/G NTT LINE | 24.08.2025 | 13:40 | 15:43 | 2:03 | INCOMING SUPPLY FAILURE FROM KADUGODI STATION DUE TO I/C FAILURE FROM EPIP 22KV END
4 | TR-2(31.5MVA) | 03.08.2025 | 6:40 | 6:45 | 0:05 | TR-2 TRIPPED ON DPR +OCR DUE TO FEEDER FAULTY, F14 FEEDERS TRIPPED ON EFR+OCR WITH JUMP CUT STN ODYS

## Formats
|  | Max peak load (other than contingency peak) recorded (MW) | Total station consumption (mu) | Date & Time DD/MMM/YY_HH;MM
|  | 17.9 | 9.124 | 02.08.2025 @ 09:00
in MU
Bank-1 | 0
Bank-2 | 8.719
Bank-2A | 0.405