## constant change
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
66/11kV MUSS,KPTCL,
statement showing energy consumptoin,peak load of - JULY - 2025
Month: JUNE - 2025
Name of the feeder | CT Ratio used | Sl.no. EM | Type of the EM |  | ENERGY CONSUMPTION | [6 empty] | NORMAL PEAK LOAD |  |  |  | CONTINGENCY PEAK LOAD |  |  |  |  | Reactive power details |  |  | Notes/Observations during the month
|  |  |  | IMP/EXP | Present Reading | Previous Reading | EM Const. | Diff. | Consump in kWh | Assessment | Total Consump in kWh | Amp | MW | Time in hr | Date | Amp | MW | Time in hr | Date | Reason for contingency peak | MVAR | Time in hr | Date
Lines | [23 empty] | Due to cable fault from BESCOM side, F-10 charged up to first bit GOS. F-23 charged on idle condition.
Line 1-Yarandanahalli 66kV line 1A (Imp) | 800/1 | KEB 02015 | C3V055 | IMP | 1047.82 | 1047.82 | 480000 | 0 | 0
| 800/1 | KEB 02015 | C3V055 | EXP | 8282.76 | 8282.76 | 480000 | 0 | 0
Line 2 Somanahalli 66kV line 2 A | 600/1 | KEB 01371 | C3V055 | IMP | 5010.57 | 5010.57 | 360000 | 0 | 0
| 600/1 | KEB 01371 | C3V055 | EXP | 6119.37 | 6119.37 | 360000 | 0 | 0
| 600/1 | Q0944392 | DLMS | EXP | 27393.6 | 21691.2 | 2000 | 5702.4 | 11404800 |  |  | 220 | 22 | 11:00 | 2025-03-07
Line 3 Somanahalli 66kV line 2 B | 300/1 | KEB 07417 | E3V051 | IMP | 7326180 | 7326180 | 180 | 0 | 0
| 300/1 | KEB 07417 | E3V051 | EXP | 2504617 | 2431478 | 180 | 73139 | 13165020
Total | [11 empty] | 237 | 23.7 | 11:00 | 2025-03-07
Transformers
Transformer-1 20 MVA 66/11 kV | 300/1 | 6605493 | ER300P |  | 443056.2 | 441190.9 | 3000 | 1865.3 | 5595900 |  |  | 97 | 9.7 | 19:00 | 2025-08-07
Transformer-2 20 MVA 66/11 kV | 200/1 | 5343960 | ER300P |  | 76677.8 | 75948.3 | 12000 | 729.5 | 8754000 |  |  | 152 | 15.2 | 10:00 | 30/7/2025
Transformer-3 20 MVA 66/11 kV | 200/1 | XD532777 | EM024 |  | 1266913.2 | 1251759.8 | 500 | 15153.4 | 7576700 |  |  | 135 | 13.5 | 17:00 | 17/7/2027
Total | [7 empty] | 0 | 21926600
[8 empty] | 0 | 0
BANK 1 | 1200/1 | Q0245844 | DLMS |  | 2415.593 | 2369.263 | 120000 | 46.33 | 5559600 |  |  | 588 | 9.7 | 19:00 | 2025-08-07 |  |  |  | 2025-08-05
F1- Jigani (U) | 400/1 | Q0245868 | DLMS |  | 2133.027 | 2100.763 | 40000 | 32.264 | 1290560 |  |  | 184 | 3 | 7:00 | 26/7/2025
F2-Harapanahalli (u) | 400/1 | Q0245957 | DLMS |  | 15.949 | 15.949 | 40000 | 0 | 0 | [10 empty] | F2 Cable faulty load shiffed to F36 jigani 220 kv station
F3- Charbhuja (u) | 400/1 | Q0245955 | DLMS |  | 518.487 | 507.88 | 40000 | 10.607 | 424280 |  |  | 48 | 0.8 | 17:00 | 2025-09-07
F4 - Indalawadi (ip) | 400/1 | Q0246076 | DLMS |  | 57.204 | 56.71 | 40000 | 0.494 | 19760 |  |  | 16 | 0.2 | 11:00 | 2025-02-07
F5- SLV (njy) | 400/1 | Q0246109 | DLMS |  | 936.147 | 919.648 | 40000 | 16.499 | 659960 |  |  | 84 | 1.4 | 7:00 | 2025-02-07 | 154 | 2.5 | 7:00 | 2025-10-07 | F7 Cable faulty load shiffed to F5 FEEDER
F6-Vabasandra (U) | 400/1 | Q245843 | DLMS |  | 507.615 | 496.703 | 40000 | 10.912 | 436480 |  |  | 56 | 0.9 | 7:00 | 2025-04-07
F7-Haragadde (U) | 400/1 | Q0246082 | DLMS |  | 612.397 | 601.958 | 40000 | 10.439 | 417560 |  |  | 60 | 1 | 9:00 | 2025-04-07
F11-Niranthara Jyothi | 400/1 | Q0245651 | DLMS |  | 29.134 | 28.944 | 40000 | 0.19 | 7600 |  |  | 8 | 0.1 | 15:00 | 2025-09-07 | [8 empty] | F-11 cable fauly 1 st bit since 22/07/2025 load shifted to F-10 IP feeder kumbarnahalli muss
F27-DNA | 200/1 | Q0246222 | DLMS |  | 1908.02 | 1883.116 | 20000 | 24.904 | 498080 |  |  | 80 | 1.3 | 10:00 | 26/7/2025
F-28 Celeprity prime layout | 400/1 | Q0245661 | DLMS |  | 772.616 | 762.874 | 40000 | 9.742 | 389680 |  |  | 52 | 0.8 | 7:00 | 2025-04-07
F29-Singh Ispat | 400/1 | Q0246073 | DLMS |  | 268.871 | 258.025 | 40000 | 10.846 | 433840 |  |  | 48 | 0.8 | 7:00 | 2025-10-07
F63-British biological | 400/1 | Q0748639 | DLMS |  | 652.3 | 604.6 | 2000 | 47.7 | 95400 |  |  | 35 | 0.5 | 10:00 | 2025-05-07
F-65-BMTC | 400/1 | Q0944365 | DLMS |  | 4927.8 | 4485.7 | 2000 | 442.1 | 884200 |  |  | 84 | 1.4 | 13:00 | 2025-03-07
B1 feeders Total | [7 empty] | 0 | 5557400
BANK 2 | 1200/1 | Q0245838 | DLMS |  | 3450.852 | 3378.624 | 120000 | 72.228 | 8667360 |  |  | 916 | 15.2 | 10:00 | 30/7/2025
F8- NJY | 200/1 | Q0245865 | DLMS |  | 17.904 | 17.739 | 20000 | 0.165 | 3300 |  |  | 4 | 0.1 | 10:00 | 2025-01-07 | [8 empty] | Meeter constant & CT ration changed 1/7/2025 | 40000 to be changed as 20000
F9- Stride Arco lab (I) | 400/1 | Q0246210 | DLMS |  | 632.244 | 616.77 | 40000 | 15.474 | 618960 |  |  | 72 | 1.2 | 19:00 | 28/7/2025
F18 - Basanth Betan (I) | 400/1 | Q0246106 | DLMS |  | 2588.049 | 2555.684 | 40000 | 32.365 | 1294600 |  |  | 148 | 2.4 | 15:00 | 16/7/2025
F20-Krishna Granite | 400/1 | Q0246195 | DLMS |  | 2202.259 | 2180.44 | 40000 | 21.819 | 872760 |  |  | 104 | 1.7 | 15:00 | 15/7/2025 | [8 empty] | Meeter constant & CT ration changed 1/7/2025 | 20000 to be changed as 40000
F23-Pearl polymer (I) | 200/1 | Q0245643 | DLMS |  | 403.726 | 403.726 | 20000 | 0 | 0
F61-Bill Forge | 400/1 | 17151030 | ER300P |  | 37080 | 36494.9 | 2000 | 585.1 | 1170200 |  |  | 136 | 2.2 | 11:00 | 30/7/2025
F10- Tulasi granite | 400/1 | Q0246066 | DLMS |  | 190.817 | 190.817 | 40000 | 0 | 0
F19- Murudeshwara | 400/1 | Q0246092 | DLMS |  | 26.263 | 0 | 40000 | 26.263 | 1050520 | 1431520
F19- Murudeshwara | 400/1 | Q0245749 | DLMS |  | 1584.171 | 1574.646 | 40000 | 9.525 | 381000 |  |  | 160 | 2.6 | 17:00 | 2025-07-07
F17-Adishakthi yallamma | 400/1 | Q0245966 | DLMS |  | 706.692 | 681.857 | 40000 | 24.835 | 993400 |  |  | 128 | 2.1 | 7:00 | 2025-09-07
F64-Micro Lab | 400/1 | q0748648 | DLMS |  | 5683.9 | 5294.9 | 2000 | 389 | 778000 |  |  | 130 | 2.1 | 8:00 | 2025-02-07
F-62- TATA Advance systems | 400/1 | Q0246114 | DLMS |  | 1198.31 | 1160.075 | 40000 | 38.235 | 1529400 |  |  | 192 | 3.2 | 12:00 | 25/7/2025
Feeders Total | Bank-2 feeders total | [7 empty] | 8692140
BANK 3 | 1200/1 | Q0245749 | DLMS |  | 47.291 | 0 | 120000 | 47.291 | 5674920 | 7523119
BANK 3 | 1200/1 | Q0246166 | DLMS |  | 3299.372 | 3287.22 | 120000 | 12.152 | 1458240 | asseased |  | 814 | 13.5 | 17:00 | 17/7/2025
F12 - Sitara | 400/1 | Q0245667 | DLMS |  | 1668.791 | 1636.516 | 40000 | 32.275 | 1291000 |  |  | 108 | 1.8 | 7:00 | 2025-05-07
F14-Aron universal (I) | 400/1 | Q0246064 | DLMS |  | 1420.447 | 1385.09 | 40000 | 35.357 | 1414280 |  |  | 192 | 3.2 | 17:00 | 2025-07-07
F-15 - NJY Kallbal | 400/1 | Q0246120 | DLMS |  | 1134.236 | 1117.187 | 40000 | 17.049 | 681960 |  |  | 100 | 1.6 | 8:00 | 21/7/2025
F16-Station auxiliary. (HT) | 200/1 | Q0246100 | DLMS |  | 12.965 | 12.719 | 20000 | 0.246 | 4920 |  |  | 1 | 0.1 | 1:00 | 2025-01-07
F16-Station auxiliary. (LT) | 150/5 | 3692060 |  |  | 6466.4 | 6338.9 | 30 | 127.5 | 3825
F21-SB-Road | 400/1 | Q0245964 | DLMS |  | 376.941 | 344.43 | 40000 | 32.511 | 1300440 |  |  | 180 | 3 | 17:00 | 21/7/2025
F22-Ambedkar I/A (I) | 400/1 | Q0246196 | DLMS |  | 2117.326 | 2072.991 | 40000 | 44.335 | 1773400 |  |  | 184 | 3 | 11:00 | 2025-09-07
F25-Nandanavana | 200/1 | Q0246126 | DLMS |  | 1012.619 | 991.459 | 20000 | 21.16 | 423200 |  |  | 60 | 1 | 8:00 | 29/7/2025
F-26 O.T.I.S | 200/1 | Q0246229 | DLMS |  | 1243.432 | 1210.87 | 20000 | 32.562 | 651240 |  |  | 96 | 1.6 | 19:00 | 2025-03-07
Bank-3 feeders total | [8 empty] | 7544265
Station peak load |  |  | Station Peak Load | [8 empty] | 2120 | 35.3 | 12:00 | 2025-05-07
ENERGY AUDIT
Line (L) | Transformer = T1+T2+T3 |  |  | Bank =B=B1+B2+B3 |  | T1 |  | T2 |  | T3 | B1 | B2 | B3 | B1 feeders | B2 feeders | B3 feeders | Feeders total
0 | 22026600 |  |  | 21750079 |  | 5595900 |  | 8754000 |  | 7576700 | 5559600 | 8667360 | 7523119 | 5557400 | 8692140 | 7544265 | 21793805
Particular | Difference |  | % Error
L-T | -5595900 |  | #DIV/0!
T-B | 276521 |  | 1.2554
T1-B1 | 36300 |  | 0.64869
T2-B2 | 86640 |  | 0.98972
T3 -B3 | 53581 |  | 0.70718
Bank- Feeders | -43726 |  | -0.20104
B1 - B1 Feeders | 2200 |  | 0.039571
B2 - B2 Feeders | -24780 |  | 0.53
B3 - B3 feeders | -21146 |  | -0.28108
|  |  | Assistant Engineer (Ele), | [10 empty] | Assistant Executive Engineer (Ele)
|  |  | 66/11 kV Sub-Station, KPTCL, | [10 empty] | Yarandanahalli Nodal, KPTCL,