## CONSUMPTION
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Details of Energy Consumption & Station Peak load For The Month of JUNE-2025 of 66/11KV MANDUR MUSS
Line no | NAME OF I/C & O/G 66/11KV Lines | TYPE OF FEEDER (INCLUDE IDLE ALSO) | BESCOM O&M SEC & SUB DIVISION | Available CTR | Connected CTR | METER MAKE |  |  | READINGS |  | DIFFERENCE IN MWH | METER CONSTANT | CONSUMPTION IN UNITS IN MU | Amps | MW | TIME | DATE
[7 empty] | SL Nos. | Mode | PRESENT IN MWH | PREVIOUS IN MWH
L1 | 66KV Line Budigere-Mandur | Incoming Line |  | 1200-800/1A | 800/1A | SECURE | X2283954 | IMPORT | 4439.9 | 2837.6 | 1602.3 | 4000 | 6.4092 | 136 | 13.6 | 10:00 | 28.6.25
TR-1 | 31.5MVA Tr-01 | TR-1 |  | 400/200/1A | 400/1A | SECURE | X2308106 | IMPORT | 2468.5 | 1606.4 | 862.1 | 4000 | 3.4484 | 82 | 8.2 | 9:00 | 28.6.25
TR-2 | 31.5MVA Tr-02 | TR-2 |  | 400/200/1A | 400/1A | SECURE | X2308104 | IMPORT | 1970.9 | 1231.5 | 739.4 | 4000 | 2.9576 | 58 | 5.8 | 9:00 | 6.6.25 | 0
TOTAL Tr-1 + Tr-2 | [12 empty] | 6.406
B1 | 11KV BANK-I |  |  | 2000-1200/1A | 2000/1A | SECURE | Q0769934 | IMPORT | 5770.4 | 3718.7 | 2051.7 | 1666.67 | 3.4195 | 495 | 8.25 | 9:00 | 28.6.25
F1 | F1- Manduru | Urban | Mandur O/M | 400/200/1A | 400/1A | SECURE | Q0931279 | EXPORT | 660.1 | 422.1 | 238 | 2000 | 0.476 | 50 | 0.83333 | 20:00 | 1.6.25
F2 | F2- Bendiganahalli | Urban | Mandur O/M | 400/200/1A | 400/1A | SECURE | Q0931282 | EXPORT | 1009.4 | 644.3 | 365.1 | 2000 | 0.7302 | 210 | 3.5 | 9:00 | 28.6.25
F3 | F3- Kattagollahalli | Urban | Mandur O/M | 400/200/1A | 400/1A | SECURE | Q0931263 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - | - | - | -
F4 | F4- Bommena halli | Urban | Mandur O/M | 400/200/1A | 400/1A | SECURE | Q0931275 | EXPORT | 2049.6 | 1328.3 | 721.3 | 2000 | 1.4426 | 165 | 2.75 | 10:00 | 28.6.25
F5 | F5- IDLE |  |  | 400/200/1A | 400/1A | SECURE | Q0931269 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - |  | - | -
F6 | F6- Gunduru | Urban | Avalahalli O&M | 400/200/1A | 400/1A | SECURE | Q0931281 | EXPORT | 1085.4 | 701.4 | 384 | 2000 | 0.768 | 176 | 2.9333 | 18:00 | 21.6.25
F7 | F7-- IDLE |  |  | 400/200/1A | 400/1A | SECURE | Q0931262 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - | - | - | -
F8 | F8-- IDLE |  |  | 400/200/1A | 400/1A | SECURE | Q0931274 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - | - | - | -
Cap.B | CAP- Bank-1 |  |  | 400/200/1A | 400/1A | SECURE | Q0931285 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - | - | - | -
Cap.B | CAP.Bank-2 |  |  | 400/200/1A | 400/1A | SECURE | Q0931280 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - | - | - | -
TOTAL CONSUMPTION OF Bank-1 FEEDERS | [12 empty] | 3.4168
B2 | 11KV BANK-II |  |  | 2000-1200/1A | 2000/1A | SECURE | Q0880785 | IMPORT | 4649.5 | 2888.1 | 1761.4 | 1666.67 | 2.9357 | 350 | 5.8333 | 9:00 | 6.6.25
F9 | F9- Byappanahalli | Urban | Doddagubbi O&M | 400/200/1A | 400/1A | SECURE | Q0931278 | EXPORT | 1946.8 | 1269.1 | 677.7 | 2000 | 1.3554 | 180 | 3 | 7:00 | 30.6.25
F10 | F10- IDLE |  |  | 400/200/1A | 400/1A | SECURE | Q0931276 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - | - | - | -
F11 | F11- Kadaagrahara | Urban | Doddagubbi O&M | 400/200/1A | 400/1A | SECURE | Q0931273 | EXPORT | 1944 | 1156.6 | 787.4 | 2000 | 1.5748 | 210 | 3.5 | 10:00 | 6.6.25
F12 | F12- IDLE |  |  | 400/200/1A | 400/1A | SECURE | Q0931264 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - | - | - | -
F13 | F13- IDLE |  |  | 400/200/1A | 400/1A | SECURE | Q0931283 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - | - | - | -
F14 | F14- IDLE |  |  | 400/200/1A | 400/1A | SECURE | Q0931270 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - | - | - | -
F15 | F15- IDLE |  |  | 400/200/1A | 400/1A | SECURE | Q0931271 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - | - | - | -
F16 | F16- Station Auxiliary |  |  | 400/200/1A | 400/1A | SECURE | Q0931267 | EXPORT | 1.5 | 1 | 0.5 | 2000 | 0.001 | - | - | - | -
Cap.B | CAP- Bank-3 |  |  | 400/200/1A | 400/1A | SECURE | Q0931261 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - | - | - | -
Cap.B | CAP.Bank-4 |  |  | 400/200/1A | 400/1A | SECURE | Q0931265 | EXPORT | 0 | 0 | 0 | 2000 | 0 | - | - | - | -
TOTAL CONSUMPTION OF Bank-2 FEEDERS | [12 empty] | 2.9312
Sl. No. | Voltages in KV | MAX | Time | Date | Min | Time | Date | Total % Losses |  |  |  | STATION PEAK
1 | 66KV | 68 | 1:00 | 4.6.25 | 63 | 10:00 | 18.6.25 | Line to Transformers |  | 0.04993% |  | Amps | MW | DATE | TIME | CONSUMPTION (B1 &B2) in MU
2 | 11 KV BANK 1 | 11.2 | 1:00 | 1.6.25 | 10.6 | 10:00 | 18.6.25 | Trf-1 to Bank-1 |  | 0.8379% |  | 820 | 13.6667 | 28.6.25 | 10:00 | 6.3552
3 | 11 KV BANK 2 | 11.2 | 1:00 | 1.6.25 | 10.6 | 10:00 | 18.6.25 | Trf-2 to Bank-2 |  | 0.7414%
[8 empty] | Bank-1 to Feeders |  | 0.07916%
. | [7 empty] | Bank-2 to Feeders |  | 0.1524%
[5 empty] | Asst Engineer(Elec.) | [7 empty] | Asst Executive Engineer(Elec.)
[5 empty] | 66/11 kV Substation | [7 empty] | Nodal Officer
[5 empty] | Mandur | [7 empty] | Hoskote
0-
.

## Assessment sheet (hidden)
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Assessement Sheet for the Month of JANUARY-2023
NOTE:
On 18.01.2023 R-ph CT of ratio 1200-800/1-1-1A flashed over at 15:20hrs and errected new CT of same ratio on 19.01.2023 AT 17:43 hrs
Assesment of Energy consumption of 11kV Bank-2A+2B+2C for the month of January-2023.
Equipment | Present | previous | Difference | M/C | Consumption
20MVA Transformer-2 | 364622.1 | 360977.6 | 3644.5 | 2000 | 7289000
11KV Bank-2A | 718.957 | 695.583 | 23.374 | 120000 | 2804880
11KV Bank-2B | 837.036 | 811.386 | 25.65 | 120000 | 3078000
11KV Bank-2C | 1546.7 | 986.8 | 559.9 | 1500 | 839850
|  |  | Total(11kV Bank-2A+2B+2C) |  | 6722730
Assessed Consumption of 11Kv Bank 2A+2B+2C = -1% loss of 20MVA Transformer-2 Consumption.
20MVA Transformer-2 Consumption=7289000. 1% loss of Transformer-2 consumption =72890
Then 11kVBank-2A+ Bank2B+Bank2C Consumption= 7289000-72890=7216110
So assessed consumption of 11kV Bank2A+2B+2C for the month of January-2023 is 7216110 units.-
Then 20MVA Transformer-2 consumption = 7289000.
11kVBank-2A+ Bank2B+Bank2C Consumption=7216110

## Bank-1B Assesment (hidden)
ENERGY ASSESSMENT FOR 11KV BANK-1B OF 66/11 KV Budigere FOR THE MONTH OF July-2023
1. Assessment of ENERGY CONSUMPTION for 11KV Bank - 1B from 15/07/2023 to 17/07/2023.
Note : On 15/07/2023 in 11KV Bank -1B (R-Ph) CT (D-core )metering wiring was not extended to Energy meter. . As per RT (N) Guidance traced the D-core metering wiring and found in D-core D12 (R-Ph) wiring there was lose contact rectified and attended the same on 17.07.2023 at 11:30 hrs.
Actual Consumption recorded from 15/07/2023 to 17/07/2023 in 11kV Bank1A and 1B.
Equipment |  | Present 17.07.23 | Previous 15.07.23 | Difference | M/C | Consumption
20MVA Transformer-1, HV side Meter reading. |  | 360936.4 | 360865 | 71.4 | 2000 | 142800
11kv Bank - 1A |  | 1114.242 | 1113.39 | 0.852 | 120000 | 102240
11kv Bank - 1B |  | 4582.5 | 4565.7 | 16.8 | 1500 | 25200
Assessed Energy Consumption of 11 kV Bank-1B (from 15.07.2023 to 17.07.2023) = Consumption of HV side of 20MVA Transformer-1.-(1% of 20MVA Transformer-1, loss)
142800-142800*1%
141372
141372 Units
Assesed consumption of 11kV Bank1A +1B= 141372
Now Assesed consumption of 11kV Bank-1B = 141372-102240
Assesed consumption of 11kV Bank-1B =39132 Units
Assessed Energy Consumption of 11 kV Bank-1B (from 15.07.2023 to 17.07.2023) - Actual Energy recordedin 11kv Bank-1B (from 15.07.2023 to 17.07.2023) =39132-25200
Assessed Energy Consumption of 11 kV Bank-1B (from 15.07.2023 to 17.07.2023) = 13932 Units
Total Consumption of 11 kV Bank-1B for the month of July is = 528150+13932
542082kwh
Assessed energy consumption =,0.542082MU.
| Asst Engineer(Elec.) |  |  |  |  | Asst Executive Engineer(Elec.)
| 66/11 kV Substation |  |  |  |  | Nodal Officer
| Budigere. |  |  |  |  | Hoskote
.

## B FORM
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
B-Form for the Month of JUNE-2025
Name of the station:66/11kV S/s MANDUR
Name of the division: TL & SS Division,BIAL BEGUR
Sl. No. | Sub-Station Name | Interface Point | Meter Type | CT Ratio | Meter SL No. | Flow Type | MF | Mode | Initial (previous) | Final (present) | Consumption in KWH | Remarks
1 | 66KV Mandur | BANK-1 | P3E | 2000/1A | Q0769934 | KPTCL | 1666.67 | IMPORT | 3718.7 | 5770.4 | 3419506.839
|  | BANK-2 | P3E | 2000/1A | Q0880785 | KPTCL | 1666.67 | IMPORT | 2888.1 | 4649.5 | 2935672.538 | -
|  | AUX meter | P3E | 400/1A | Q0931267 | KPTCL | 2000 | EXPORT | 1 | 1.5 | 1000 | -
Annexure
Sl. No. | Sub-Station Name | Transformer | Meter Type | CT Ratio | Meter SL No. | Flow Type | MF | Mode | Initial | Final | Consumption in KWH | Remarks
1 | 66KV Mandur | Transformer -1 | E3M024 | 400/1A | X2308106 | KPTCL | 4000 | IMPORT | 1606.4 | 2468.5 | 3448400 | -
|  | Transformer -2 | E3M024 | 400/1A | X2308104 | KPTCL | 4000 | IMPORT | 1231.5 | 1970.9 | 2957600 | -
NOTE: (IF ANY ASSESMENT /REPLACEMENT OF CT&PT/CHANGE IN CT RATIO/CHANGE IN METER/METER CONSTANT):
Asst Engineer(El.) |  |  |  | Asst Executive Engineer (El) |  |  |  |  | Executive Engineer(El)
66/11 KV Substation,KPTCL |  |  |  | Nodal Officer,KPTCL |  |  |  |  | TL&SS Division,KPTCL
Mandur |  |  |  | Hoskote |  |  |  |  | BIAL Begur

## BANK TO FEEDER LOSSES
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Bank to Feeder Losses For the Month of JUNE- 2025of 66/11KV MANDUR MUSS
| Sl No | Name of the Station | Bank/ Feeder | Readings |  |  | Constant | Net Consumption in KWH
|  |  |  | Previous | Present | Difference
| 1 | 66/11KV MANDUR | Bank - 1 | 3718.7 | 5770.4 | 2051.7 | 1666.67 | 3419506.839
| 2 |  | F1- Manduru | 422.1 | 660.1 | 238 | 2000 | 476000 | 3416800
| 3 |  | F2- Bendiganahalli | 644.3 | 1009.4 | 365.1 | 2000 | 730200
| 4 |  | F3- Kattagollahalli | 0 | 0 | 0 | 2000 | 0
| 5 |  | F4- Bommena halli | 1328.3 | 2049.6 | 721.3 | 2000 | 1442600 |  |  | Total losses
| 6 |  | F5- IDLE | 0 | 0 | 0 | 2000 | 0 |  | 1 | Bank-1 to feeder losses = | #REF!
| 7 |  | F6- Gunduru | 701.4 | 1085.4 | 384 | 2000 | 768000
| 8 |  | F7-- IDLE | 0 | 0 | 0 | 2000 | 0 |  | 2 | Bank-2A to feeder losses = | #REF!
| 9 |  | F8-- IDLE | 0 | 0 | 0 | 2000 | 0 | 0
| 10 |  | CAP- Bank-1 | 0 | 0 | 0 | 2000 | 0
| 11 |  | CAP.Bank-2 | 0 | 0 | 0 | 2000 | 0
12
| 13 |  | Bank - 2 | 2888.1 | 4649.5 | 1761.4 | 1666.67 | 2935672.538
| 14 |  | F9- Byappanahalli | 1269.1 | 1946.8 | 677.7 | 2000 | 0
| 15 |  | F10- IDLE | 0 | 0 | 0 | 2000 | 0
| 16 |  | F11- Kadaagrahara | 1156.6 | 1944 | 787.4 | 2000 | 1574800
| 17 |  | F12- IDLE | 0 | 0 | 0 | 2000 | 0
| 18 |  | F13- IDLE | 0 | 0 | 0 | 2000 | 0
| 19 |  | F14- IDLE | 0 | 0 | 0 | 2000 | 0
| 20 |  | F15- IDLE | 0 | 0 | 0 | 2000 | 0
| 21 |  | F16- Station Auxiliary | 1 | 1.5 | 0.5 | 2000 | 1000
| 22 |  | CAP- Bank-3 | 0 | 0 | 0 | 2000 | 0
| 23 |  | CAP.Bank-4 | 0 | 0 | 0 | 2000 | 0

## ALDC INTERRUPTION FORMAT
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
|  |  | ALDC INTERRUPTION FORMAT FOR THE MONTH OF JUNE-2025 | [16 empty] | Note:
2025-06-01
SL NO | CIRCLE | DIVISION NAME | STATION NAME_SCADA | 11kV FEEDERS Asper SCADA | 11kV FEEDERS ACTUAL(INCLUDE IDLE FEEDERS ALSO) | CATEGORY(RURAL/URBAN/IP/INDUSTRIAL/NJY) | BESCOM SUB DIVISION & O&M UNIT COVERED | PEAK LOAD IN MW | TIME | DATE | Schedule Interruption |  |  |  | Un-schedule Interruption |  |  |  | Remarks if any changes in 11kV Feeders to be highlightnened | Please include if there is any new feeders/change in the feeder name/category other than the list mentioned below and highlight the same
[11 empty] | KPTCL PART(L/C) |  | BESCOM PART(SL/S) |  | KPTCL PART(B/F, ULS,L/C, MSF, HT) |  | BESCOM PART(L/C, L/R, L/T)
[11 empty] | Nos. | Duration | Nos. | Duration | Nos. | Duration | Nos. | Duration
1 | BRAZ | Bial | MANDUR |  | F1- Manduru | Urban | MANDUR | 0.83333 | 20:00 | 1.6.25 | 0 | 0:00 |  |  | 6 | 9:51 |  |  |  | - | - | - | - | -
2 | BRAZ | Bial | MANDUR |  | F2- Bendiganahalli | Urban | MANDUR | 3.5 | 9:00 | 28.6.25 | 0 | 0:00 |  |  | 14 | 14:28 |  |  |  | - | - | - | - | -
3 | BRAZ | Bial | MANDUR |  | F3- Kattagollahalli | Urban | MANDUR | - | - | - | 0 | 0:00 |  |  | - | - |  |  |  | - | - | - | - | -
4 | BRAZ | Bial | MANDUR |  | F4- Bommena halli | Urban | MANDUR | 2.75 | 10:00 | 28.6.25 | 0 | 0:00 |  |  | 9 | 12:11 |  |  |  | - | - | - | - | -
5 | BRAZ | Bial | MANDUR |  | F5- IDLE | - | - | 0 | - | - | 0 | 0:00 |  |  | - | - |  |  |  | - | - | - | - | -
6 | BRAZ | Bial | MANDUR |  | F6- Gunduru | Urban | AVALAHALLI | 2.9333 | 18:00 | 21.6.25 | 0 | 0:00 |  |  | 10 | 13:11 |  |  |  | - | - | - | - | -
7 | BRAZ | Bial | MANDUR |  | F7-- IDLE | - | - | - | - | - | 0 | 0:00 |  |  | - | - |  |  |  | - | - | - | - | -
8 | BRAZ | Bial | MANDUR |  | F8-- IDLE | - | - | - | - | - | 0 | 0:00 |  |  | - | - |  |  |  | - | - | - | - | -
9 | BRAZ | Bial | MANDUR |  | F9- Byappanahalli | Urban | Dodda Gubbi | 3 | 7:00 | 30.6.25 | 0 | 0:00 |  |  | - | - |  |  |  | - | - | - | - | -
10 | BRAZ | Bial | MANDUR |  | F10- IDLE | - | - | - | - | - | 0 | 0:00 |  |  | - | - |  |  |  | - | - | - | - | -
11 | BRAZ | Bial | MANDUR |  | F11- Kadaagrahara | Urban | Dodda Gubbi | 3.5 | 10:00 | 6.6.25 | 0 | 0:00 |  |  | 13 | 22:44 |  |  |  | - | - | - | - | -
12 | BRAZ | Bial | MANDUR |  | F12- IDLE | - | - | - | - | - | 0 | 0:00 |  |  | - | - |  |  |  | - | - | - | - | -
13 | BRAZ | Bial | MANDUR |  | F13- IDLE | - | - | - | - | - | 0 | 0:00 |  |  | 9 | 12:56 |  |  |  | - | - | - | - | -
14 | BRAZ | Bial | MANDUR |  | F14- IDLE | - | - | - | - | - | 0 | 0:00 |  |  | - | - |  |  |  | - | - | - | - | -
15 | BRAZ | Bial | MANDUR |  | F15- IDLE | - | - | - | - | - | 0 | 0:00 |  |  | - | - |  |  |  | - | - | - | - | -
16 | BRAZ | Bial | MANDUR |  | F16- Station Auxiliary | Urban |  | - | - | - | 0 | 0:00 |  |  | - | - |  |  |  | - | - | - | - | -

## INTERRUPTION
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Interruptions statements of 66/11kV S/S MANDUR for the month of JUNE-2025.
Name of zone: Bangalore, Circle:BRAZ, District: Bangalore Urban
Sl. No | Feeder Name | LINE CLEAR |  | LINE FAULTY | [7 empty] | Total Interruption for Line faults |  | MSF |  | LOAD SHEDDING |  |  |  | Three Phase Supply given |  | Total Interruption(L/F+L/C+MSF+ULS) |  | Targeted Three Phase
|  | NO'S | Duration | EFR |  | OCR |  | EFR&OCR |  | PRV/Distance/ Differential/ REFR/86 Relay/HT | [5 empty] | SCHEDULED |  | UNSCHEDULED
|  |  |  | NO'S | Duration | NO'S | Duration | NO'S | Duration | NO'S | Duration | NO'S | Duration | NO'S | Duration | NO'S | Duration | NO'S | Duration | NO'S | Duration | NO'S | Duration | NO'S | Duration
1 | 66kV I/C Line Budigere | 1 | 7:22 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 30 | 712:38 | 1 | 7:22 | 30 | 720:00 | 720:00
3 | 31.5MVA Tr-1 | 1 | 7:22 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 30 | 712:38 | 1 | 7:22 | 30 | 720:00 | 720:00
4 | 31.5MVA Tr-2 | 1 | 7:22 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 30 | 712:38 | 1 | 7:22 | 30 | 720:00 | 720:00
5 | 11kV Bank-1 | 1 | 7:22 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 30 | 712:38 | 1 | 7:22 | 30 | 720:00 | 720:00
6 | 11kV Bank-2 | 1 | 7:22 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 30 | 712:38 | 0 | 7:22 | 30 | 720:00 | 720:00 |  | #REF! | 0:00
9 | F1- Manduru | 6 | 9:51 | 3 | 0:14 | 2 | 0:25 | 1 | 0:05 | 0 | 0:00 | 6 | 0:44 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 30 | 709:25 | 0 | 10:35 | 30 | 720:00 | 720:00 | *
10 | F2- Bendiganahalli | 14 | 14:28 | 14 | 2:41 | 7 | 1:32 | 1 | 0:09 | 0 | 0:00 | 22 | 4:22 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 30 | 701:10 | 0 | 18:50 | 30 | 720:00 | 720:00
11 | F3- Kattagollahalli | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
12 | F4- Bommena halli | 9 | 12:11 | 8 | 1:37 | 3 | 3:05 | 1 | 0:05 | 0 | 0:00 | 12 | 4:47 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 30 | 703:02 | 0 | 16:58 | 30 | 720:00 | 720:00
13 | F5- IDLE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14 | F6- Gunduru | 10 | 13:11 | 27 | 6:10 | 2 | 0:15 | 4 | 1:47 | 0 | 0:00 | 33 | 8:12 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 30 | 698:37 | 0 | 21:23 | 30 | 720:00 | 720:00
15 | F7-- IDLE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
16 | F8-- IDLE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
17 | Capacitor Bank-1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
18 | Capacitor Bank-2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19 | F9- Byappanahalli | 13 | 22:44 | 27 | 4:59 | 21 | 5:47 | 6 | 2:18 | 0 | 0:00 | 54 | 13:04 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 30 | 684:12 | 0 | 35:48 | 30 | 720:00 | 720:00
20 | F10- IDLE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
21 | F11- Kadaagrahara | 9 | 12:56 | 15 | 2:50 | 7 | 1:09 | 15 | 2:45 | 0 | 0:00 | 37 | 6:44 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 30 | 700:20 | 0 | 19:40 | 30 | 720:00 | 720:00
22 | F12- IDLE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
23 | F13- IDLE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
24 | F14- IDLE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
25 | F15- IDLE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
26 | F16- Station Auxiliary | 1 | 7:22 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 30 | 712:38 | 0 | 7:22 | 30 | 720:00 | 720:00
27 | Capacitor Bank-3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
28 | Capacitor Bank-4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | Asst Engineer(Elec.) | [6 empty] | Asst Executive Engineer(Elec.) | [8 empty] | Executive Engineer(ele)
|  | 66/11 kV Substation | [6 empty] | Nodal Officer | [8 empty] | TL&SS Division
|  |  | Mandur | [5 empty] | Hoskote | [8 empty] | BIAL

## INT.IC&TR
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Outages of I/C LINES, 20 MVA Tr-1 & 2 for the month JUNE -2025 of 66/11KV MANDUR MUSS
Sl.No | Date | From | To | Duration | Remarks/Reason
INCOMING LINES (SCHEDULED -LCs)
1 | 22.06.2025 | 10:00 | 17:22 | 7:22 | Availed LC for carrying out 1st quarterly maintenance work
INCOMING LINES (UNSCHEDULED -LC,LTs, MSF)
OUTGOING LINES (UNSCHEDULED -LTs, MSF)
1 | - | - | - | - | NIL
20MVA TR-1(SCHEDULED-LC)
Sl.No | Date | From | To | Duration | Remarks/Reason
1 | 22.06.2025 | 10:00 | 17:22 | 7:22 | Availed LC for carrying out 1st quarterly maintenance work
20MVA TR-1(UNSCHEDULED-LC,MSF,LT)
Sl.No | Date | From | To | Duration | Remarks/Reason
1 | NIL | NIL | NIL | NIL | NIL
20MVA TR-2(SCHEDULED-LC)
Sl.No | Date | From | To | Duration | Remarks/Reason
1 | 22.06.2025 | 10:00 | 17:22 | 7:22 | Availed LC for carrying out 1st quarterly maintenance work
20MVA TR-2(UNSCHEDULED-LC,MSF,LT)
Sl.No | Date | From | To | Duration | Remarks/Reason
Assistant Engineer(Elec.)
66/11KV Substation, KPTCL
Mandur

## MORETHAN 10TIMES INTERR
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
MORETHAN 10 TIME INTERRUPTION OF JUNE-2025
Sl No | 11KV Feeders | No of Times tripping due to line troubles(LTs) + L/C | Duration
1 | F1- Manduru | 0 | 10:35
2 | F2- Bendiganahalli | 0 | 18:50
3 | F3- Kattagollahalli | - | -
4 | F4- Bommena halli | 0 | 16:58
5 | F5- IDLE | - | -
6 | F6- Gunduru | 0 | 21:23
7 | F7-- IDLE | - | -
8 | F8-- IDLE | - | -
9 | F9- Byappanahalli | 0 | 35:48
10 | F10- IDLE | - | -
11 | F11- Kadaagrahara | 0 | 19:40
12 | F12- IDLE | - | -
13 | F13- IDLE | - | -
14 | F14- IDLE | - | -
15 | F15- IDLE | - | -
16 | F16- IDLE | 0 | 7:22
NO OF OVERLOAD FEEDERS DURING THE MONTH OF APRIL--2025
SL.NO | NAME OF THE MUSS | NAME OF THE SUB-DIV | NAME OF THE SECTION | Details of overload feeders
| MANDUR | - | - | - | -
1
NO OF IDLE FEEDERS DURING THE MONTH OF APRIL-2025
SL.NO | NAME OF THE MUSS | NAME OF THE SUB-DIV | NAME OF THE SECTION | Details of idle feeders
1 | MANDUR | - | - | 8Nos
Assistant Engineer(Elec.)
66/11KV S/s, KPTCL
Mandur

## tfr trippings
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
DETAILS OF POWER TRANSFORMER TRIPPINGS DUE TO 11KV FEEDER FAULTS IN THE MONTH OF JUNE-2025
SL NO. | NAME OF THE STATION | POWER TRANSFORMER | DATE | TIME | RELAY ON WHICH TR TRIPPED | RELAY ON WHICH FEEDER TRIPPED | RELAY ON WHICH BANK TRIPPED | DETAILS OF TRIPPING |  |  | ACTION TAKEN
1 | 66/11kv Mandur | NILL
Assistant Engineer(Elec.)
66/11kV S/s, KPTCL
MANDUR

## OVER LAP TRIPPINGS
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Statement showing the details of overlap trippings of Transformers/Banks JUNE-2025
Sl.No | Name of the Division | Name of the Station | Transformer No. | Transformer Capacity | Tripping Details |  | Feeder tripping details along with Transformer or Bank | Transformer | [7 empty] | Bank |  |  | Feeder Relay Details | [7 empty] | Feeder master trip operated Yes/No | Feeder breaker tripped or Not | Remarks
[5 empty] | Date | Time |  | R Phase OCR |  | Y Phase OCR |  | B Phase OCR |  | EFR |  | R phase OCR | B Phase OCR | EFR | R Phase OCR |  | B Phase OCR |  | Y Phase OCR |  | EFR
[8 empty] | IDMT | High Set | IDMT | High Set | IDMT | High Set | IDMT | High Set | IDMT | IDMT | IDMT | IDMT | High Set | IDMT | High Set | IDMT | High Set | IDMT | High Set
1 | Bial | Mandur | NIL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## MONTHLY WORKS
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
MONTHLY WORKS REPORT OF BRAZ CIRCLE FOR JUNE- 2025
R&M WORKS
TABLE-A Details regarding the newly commissioned Transformers or Equiments /Erection or Installation/APW/ GCW works carried out in various stations of BRAZ Circle
Sl.No | Name of the Division | Name of the Station | Name of the work | Voltage Class | Nomenclature of the Equipment | Make , Serial No. and Specifications | Date of Commission/ Erection | Remarks if any
1 | BIAL | MANDUR | NIL
TABLE-B Details regarding replacement works in existing equipments carried out in various stations of BRAZ Circle
Sl.No | Name of the Division | Name of the Station | Name of the work | Voltage Class | Nomenclature of the Equipment | Make , Serial No. and Specifications | Date of Replacement / Erection | Remarks if any
1 | BIAL | MANDUR | NIL
Note: Please furnish the above sought details of the works carried out within 5 th of every month without fail ,in future.

## EQUIPMENTS FAILED
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Details of equipment failure of BIAL BEGUR Division for the month of JUNE-2025
1 | Name of substation | 66/11KV Mandur | -
2 | Utility/Owner of substation | KPTCL | -
3 | Faulty Equipment | - | -
4 | Details of replaced equuipment | - | -
5 | Rating | - | -
6 | Make | - | -
7 | Sr No | - | -
8 | Year of manufacturing | - | -
9 | Year of commissioning | - | -
10 | Date and time of occurrence/discovery of fault | - | -
11 | Fault discovered during | - | -
12 | Present condtion of equipment | - | -
13 | Details of previous maintenance | - | -
14 | Details of previous failure | - | -
15 | Sequence of events/Description of fault | - | -
16 | Details of tests done after failure | - | -
17 | Conclusion/recommendations | - | -
| NOTE: | MENTION ANY EQUIPMENT FAILED LIKE 66kV and 11kV CTs,PTs,Relays,Potheads etc;

## Station Losses (hidden)
KARNATAKA POWER TRANSMISSIN CORPORATION LIMITED
STATION losses for the month of MARCH--2025
Line no | NAME OF I/C & O/G 66/11KV Lines | READINGS |  | DIFFERENCE | METER CONSTANT | CONSUMPTION IN UNITS IN MU | Transmission Losses in %age
|  | PRESENT | PREVIOUS
L1 | 66KV Budigere-Mandur | #REF! | #REF! | #REF! | 4000 | #REF!
| TOTAL Consumption of 66kV Incoming Lines |  |  |  |  | #REF!
TR-1 | 31.5MVA Tr-01 | 2468.5 | 1606.4 | 862.1 | 4000 | 3.4484 | #REF! | (Line to Trfr) | Line to Trfr
TR-2 | 31.5MVA Tr-02 | 1970.9 | 1231.5 | 739.4 | 4000 | 2.9576 | #REF! |  | #REF!
| TOTAL Consumption of 20MVA Transformers |  |  |  |  | 6.406 |  |  | Total Trfr to total Bank
B-1 | 11kV Bank-1 | #REF! | #REF! | #REF! | 1666.67 | #REF! | #REF! | (Bank to Feeders) | #REF!
B-2 | 11kV Bank-2 | #REF! | #REF! | #REF! | 1666.67 | #REF! | #REF!
| TOTAL 11KV Banks (1+2) |  |  |  |  | #REF! |  |  | Total B2A to FDRS
B-1 Fdrs | TOTAL CONSUMPTION OF FEEDERS ON B-1 |  |  |  |  | 3.4168 |  |  | #REF!
B-2 Fdrs | TOTAL CONSUMPTION OF FEEDERS ON B-2 |  |  |  |  | #REF! |  |  | Total B2B to FDRS
| TOTAL CONSUMPTION OF ALL FEEDERS |  |  |  |  | #REF!
STATION LOSS:
L1 | 66KV Line-1 Incoming Budigere | #REF! | #REF! | #REF! | 2000 | #REF!
B-1 | 11kV Bank-1A | #REF! | #REF! | #REF! | 120000 | #REF!
B-2 | 11kV Bank-1B | #REF! | #REF! | #REF! | 1500 | #REF!
[5 empty] | Station loss | #REF!

## Transmission losses (hidden)
Transmission Line and station losses for the month of APRIL-2025
66/11Kv Mandur S/s Line Losses
L-1 = 66KV Line-1 Budigere-Mandur
|  |  | Budigere |  | Sending End | [5 empty] | Receiving End |  |  |  | Mandur
Sl.No | Month/Year | 66kv Line Begur-Budigere |  | Present(FR) | Previous (IR) | Diff | M/C | Export Energy in MU ( A) | 66kv Line Begur-Budigere |  | Present(FR) | Previous (IR) | Diff | M/C | Export Energy in MU (B) | Losses C=(A-B) | Line losses (A-B)*A/100 | %Losses (C/ Exp)*100
1 | 2025-04-01 | L-1 | EXPORT |  | 550390 | -550390 | 4000 | -2201.56 | L-1 | IMP | #REF! | 2837.6 | #REF! | 4000 | #REF! | #REF! | #REF! | #REF!
[7 empty] | (A) | #REF! | [5 empty] | (B) | #REF!
| IF Points | [10 empty] | Mandur station Transmission losses
|  |  | Present | Previous | Diff | M/C | Consumption In KWH
| 11kV Bank-1 |  | #REF! | #REF! | #REF! | 1666.67 | #REF! |  |  |  |  | Sending End |  | Receiving End
| 11kV Bank-2 |  | #REF! | #REF! | #REF! | 1666.67 | #REF! |  |  |  |  | Export Energy in MU (A) |  | IF Points Consumption (B) |  | Station Loss= (A-B)/A*100 |  | Stn Loss
[11 empty] | 2025-04-01 | #REF! |  | #REF! |  | #REF! |  | -0.9
[6 empty] | (B1) | #REF!

## aSSESMENT (hidden)
ENERGY ASSESSMENT FOR 11KV BANK-1A OF 66/11 KV Budigere FOR THE MONTH OF SEPTEMBER-2024
1. Assessment of ENERGY CONSUMPTION for 11KV Bank-1A on 01.09.2024
Note : On 01/09/2024 in 11KV Bank -1A Energy Meter was found faulty so the faulty Energy meter was replaced by New meter at 15:00hrs.
Actual Consumption recorded on 01/09/2024 in 11kV Bank1A and 1B.
Equipment | Present | Previous | Difference | M/C | Consumption
20MVA Transformer-1, HV side Meter reading. | 388608.3 | 388536.5 | 71.8 | 2000 | 143600
11kv Bank - 1A | 0.287 | 0 | 0.287 | 120000 | 34440
11kv Bank - 1B | 12360.3 | 12331.4 | 28.9 | 1500 | 43350 | 77790
Actual Consumption recorded in 20MVA Transformer-1 = 143600 kwh
Actual Consumption recorded in 11kV Bank-1B = 43350 kwh
So Consumption recorded in 20 MVA Transformer-1 - Actual recorded consumption in 11kV Bank-1B = 143600-43350 =100250 kwh
Now 20MVA Transformer-1 consumption - 1% of 20MVA transformer loss
100250-100250*1% = 1002.5 units
Assesed consumption of 11kV Bank1A =( Actual consumption recorded in Transformer-1 - Actual consumptin recorded in 11kV Bank-1B)-1% of 20MVA Transformer loss
So assessed consumption of 11kV Bank-1A = 100250 - 1002.5 = 99247.5 Units
Assessed Energy Consumption of 11 kV Bank-1A on 01.09.2024 is 99247.5 UNITS
Assessed energy consumption = 0.0992475 MU.
Total Consumption of 11 kV Bank-1A after assessement for the month of SEPTEMBER -2024 is = 3356400+ 992475 = 3455647.5 kwh