## 3712 KVA HT INST SULIBELE ( (4)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
| ESTIMATE No : | SOS/MA/HT- |  |  | DATE :
ESTIMATE FOR ARRANGING POWER SUPPY TO HT INSTALLATION TO AN EXTENT OF 350 KVA FOR INDUSRIAL PURPOSE IN FAVOUR OF M/S APTIV COMPONENTS INDIA PVT LTD, ( LESSOR), SITUATED AT PROPERTY NO 66, BLOCK 'F' INSIDE THE PREMISES OF HSK LOGISTICS ASSESTS INDIA PVT LTD. ( EXISTING 3712 KVA HT INSTALLATION BEARING RR NO NGHT 54 + OTHER PROPOSED HT INSTALLATION OF 3333 KVA SUBMITTED FOR SANCTION + THIS PROPOSED LOAD OF 350 KVA, AND THE TOTAL LOAD IS 7395 KVA IN THE SAME PREMISES OF HSK LOGISTICS ASSESTS INDIA PVT LTD), AT KADIRANAPURA VILLAGE, SULIBELE HOBLI, HOSAKOTE TALUK, BANGALORE RURAL DISTRICT. IN SULIBELE O&M UNIT OF NADAGUDI SUB DIVISION, HOSAKOTE DIVISION.
UNDER SELF EXECUTION | [9 empty] | 3712
PART A : PROVIDING RMU & EXTENSION OF 11 KV LINE USING 3X95 SQMM XLPE UG CABLE USING CONVENTIONAL LAYING WITH EXCAVATION OF SOIL. | [9 empty] | 3333
SL. NO. | PARTICULRS | MATERIAL CODE | UNIT | QTY | MATERIAL COST |  | LABOUR COST |  |  | 350
[5 empty] | RATE | AMOUNT | RATE | AMOUNT |  | 7395
1 | Providing Compact RMU 11 kV Class SF6/VCB Type (1 OD) | CDS- 34 | UNIT | 1 | 201218 | 201218 | 4925 | 4925
2 | Providing Compact RMU 11 kV Class SF6/VCB Type (1 VL) | CDS- 35 | UNIT | 1 | 201218 | 201218 | 4925 | 4925
3 | 11kV Class 3x95 Sqmm XLPE UG Cable (Round Armoured) | 287400 | KM's | 0.8 | 889666 | 711732.8
4 | Cable Termination Kit Indoor HS Type Suitable for 3x95 Sq. mm Cable | 288332 | No's | 3 | 3744 | 11232
5 | Cable covering Tiles | CDS 19 | No's | 3200 | 10.25 | 32800
6 | Artificial / Manufacture sand | 800651 | cmt | 48 | 1786 | 85728
7 | RCC Hume pipe, 2000 mm long, 150 mm dia | 820672 | Nos | 10 | 307 | 3070
8 | Collars for RCC Hume pipe 150 mm dia | 820703 | Nos | 10 | 82 | 820
9 | G.I Pipe 100 mm dia for Cable raising for drain crossing, Cable raising etc., | 768052 | mtr | 10 | 1235 | 12350
10 | Route and joint indicating stones | 802460 | Nos | 20 | 133 | 2660
11 | Labour Charges | [7 empty] | 227.5
| a) Cable trench excavation, 800x0.60x1=480, Ordinary soil | As per CDS-2023-24 | Cmt | 480 |  |  | 262 | 125760
| b) Laying of cable in trench |  | km | 0.8 |  |  | 61322 | 49057.6
| c) Refilling and consolidation |  | Cmt | 450 |  |  | 160 | 72000
| e) Making of cable terminations |  | No | 3 |  |  | 2658 | 7974
| f) Covering the cable with tiles |  | km | 0.8 |  |  | 4367 | 3493.6
| g) Spreading Sand and forming with Sand round the cable |  | km | 0.8 |  |  | 14810 | 11848
| h) Laying of RCC hume pipe |  | mtr | 20 |  |  | 69 | 1380
| i) Laying of GI Pipe |  | mtr | 10 |  |  | 93 | 930
| j) Laying of Route indicating stones |  | No | 20 |  |  | 116 | 2320
12 | Misc. Materials and Labour |  | LS |  |  | 2171.2 |  | 1386.8
| PART 'A' : Material cost |  |  |  |  | 1265000
| PART 'A' : Labour charges | [6 empty] | 286000
PART 'B' :H.T.METERING CUBICLE WITH 3 PH 4 WIRE USING 3 PT'S & 3 CT'S.
SL.NO | NAME OF THE MATERIALS | MATERIAL CODE | UNIT | QTY | RATE | AMOUNT | LABOUR CHARGES
[7 empty] | RATE | AMOUNT
1 | 11 KV, HT Metering cubicle of different CT Ratio, Both side cable entry type with 3CT 3PT's with Transparent Cover TTB with 30x8 mm Cu Bus bars. With Modem and 2 nos of meters for 3 Phase 4 wire Metering without Load Break Switch (HT Metering Box Fabricated out of 3mm MS sheet duly epoxy powder coated) as per revised specification (DwgNo.BESCOM/GM/QS&S/ Dtd 24.11.2018 ) CT Ratio 20/1 Amps | 358351 | Unit | 1 | 243472 | 243472 | 1844 | 1844
2 | Construction of platform with size stone, cement concrete for erection of Metering cubicle including material + labour charges | 4.06 | per structure | 1 |  |  | 30361 | 30361
3 | Earthing materials pipe type for grounding as per Drawing No. BESCOM/GM/CP/15 & 34/Dt: 24.10.07. | 281674 ,600095 & 607054 | SET | 4 | 1729 | 6916 | 949 | 3796
4 | Misc Materials and Labour |  | LS |  |  | 612 |  | 999
| PART 'B' : Material cost |  |  |  |  | 251000
| PART 'B' : Labour charges | [6 empty] | 37000
ABSTRACT |  |  |  |  | Material cost |  | Labour Cost
PROVIDING RMU & EXTENSION OF 11 KV LINE USING 3X95 SQMM XLPE UG CABLE USING CONVENTIONAL LAYING WITH EXCAVATION OF SOIL. |  |  | PART 'A' |  | 1265000 |  | 286000
H.T.METERING CUBICLE WITH 3 PH 4 WIRE USING 3 PT'S & 3 CT'S. |  |  | PART 'B' |  | 251000 |  | 37000
TOTAL |  |  |  |  | 1516000 |  | 323000
TYPICAL COST DATA SHEET FOR SELF EXECUTION WORK
SL NO | PARTICULARS | [6 empty] | AMOUNT IN Rs
1 | MATERIAL COST | [6 empty] | 1516000
2 | LABOUR CHARGES | [6 empty] | 323000
3 | BASIC RATE ( SUM OF SL NO 1&2 ) | [6 empty] | 1839000
4 | AREA SPECIFIC LOADING ON BASIC RATES (SL NO 3) WHEREVER APPLICABLE | [6 empty] | 55170
5 | APPLICABLE GST ON SUM OF SL NO 3 & 4 | [6 empty] | 340950.6
6 | COST OF ESTIMATE (SUM OF SL NO 3 TO 5) | [6 empty] | 2235120.6
7 | STATUTORY CHARGES AS PER ACTUAL | [6 empty] | 5000
| TOTAL ESTIMATE COST | [6 empty] | 2235120.6
CERTIFICATE
Certified that I have personally inspected the spot and prepared the estimate as per SR 2023-24 for most economical & safe way of execution.
REPORTS
THIS ESTIMATE AMOUNTING Rs. 22,35,121/-ONLY HAS BEEN PREPARED FOR ARRANGING POWER SUPPY TO HT INSTALLATION TO AN EXTENT OF 350 KVA FOR INDUSRIAL PURPOSE IN FAVOUR OF M/S APTIV COMPONENTS INDIA PVT LTD, ( LESSOR), SITUATED AT PROPERTY NO 66, BLOCK 'F' INSIDE THE PREMISES OF HSK LOGISTICS ASSESTS INDIA PVT LTD. ( EXISTING 3712 KVA HT INSTALLATION BEARING RR NO NGHT 54 + OTHER PROPOSED HT INSTALLATION OF 3333 KVA SUBMITTED FOR SANCTION + THIS PROPOSED LOAD OF 350 KVA, AND THE TOTAL LOAD IS 7395 KVA IN THE SAME PREMISES OF HSK LOGISTICS ASSESTS INDIA PVT LTD ), AT KADIRANAPURA VILLAGE, SULIBELE HOBLI, HOSAKOTE TALUK, BANGALORE RURAL DISTRICT. IN SULIBELE O&M UNIT OF NADAGUDI SUB DIVISION, HOSAKOTE DIVISION.
In this estimate the following works are proposed as shown in the sketch.
[1] PART 'A' : PROVIDING RMU & EXTENSION OF 11 KV LINE USING 3X95 SQMM XLPE UG CABLE USING CONVENTIONAL LAYING WITH EXCAVATION OF SOIL.
1 | Point 'A' |  | Tapping point at existing 3 way RMU of F9 HSK LOGISTIC Feeder emanating from 66/11 KV Sulibele MUSS, by Providing Compact RMU 11 kV Class SF6/VCB Type (1 OD) & (1 VL)
2 | Point A to B |  | Extension of 11 KV line using 3X95 Sq mm XLPE UG Cable using to an extent of 0.8 km from existing 3 way RMU near NGHT 54 HT installation.
[2] PART 'B' :H.T.METERING CUBICLE WITH 3 PH 4 WIRE USING 3 PT'S & 3 CT'S.
3 | Point 'B' |  | Erection of 11 KV, HT Metering cubicle of different CT Ratio, Both side cable entry type with 3CT 3PT's with Transparent Cover TTB with 30x8 mm Cu Bus bars. With Modem and 2 nos of meters for 3 Phase 4 wire Metering without Load Break Switch (HT Metering Box Fabricated out of 3mm MS sheet duly epoxy powder coated) as per revised specification (DwgNo.BESCOM/GM/QS&S/ Dtd 24.11.2018 ) CT Ratio 20/1 Amps by constructing platform.
The power supply requested by the applicant for arranging power supply to an extent of 350 KVA, to cater the load it is proposed from existing F9 HSK Logistic feeder from 66/11 KV Sulibele Sub-station, having 3x400 sq mm UG Cable The peak load of the feeder is 2.83 MW . The Sub-station installed capacity 1x 20 MVA +1x 12.5 MVA. The peak load of the station is 20 MW. And this existing station which is about 3.5 KM distance from the applicant premises.
The total load calculation in the same premises
1 | NGHT 54 | 3712 KVA |  |  | Applicant provided new PCVCB switchgear panel at 66/11 KV Sulibele sub-station under self execution. And new feeder drawn using 3x400 sqmm XLPE for the distance of 3.5 km up to applcant premises |  |  | commissioned
2 | Proposed another HT installation. | 3333 KVA |  |  | It is proposed new feeder from 220/66/11 KV Haraluru Muddenahalli R/S By providing new switchgear panel and to drawing new 11 kv feeder using 3x400 sqmm XLPE for the distance of 5.175 km up to applcant premises. |  |  | Estimate submitted
3 | Proposed this HT installation | 350 KVA |  |  | Tapping point at existing 3 way RMU of F9 HSK LOGISTIC Feeder emanating from 66/11 KV Sulibele MUSS, by Providing Compact RMU 11 kV Class SF6/VCB Type (1 OD) & (1 VL). |  |  | Estimate submitted
| TOTAL LOAD EXISTING + PROPOSED IN THE SAME PREMISES | 7395 KVA
In future, if the total load requirement exceeds 7500 KVA then the applicant / developer shall establish 66/11 KV substation at their own cost in the above premises under self-execution and avail power supply on 66 kv EHT basis as per KERC regulations.
All necessary permissions / NOC / Approvals from Electrical Inspectorate, , PWD, KPTCL, BSNL, & local panchayath office for laying UG Cable, obtain by the applicant at their own cost duly observing the all legal formalities.
The detailed estimate is based on the BESCOM SR 2023-24 with GST. The work is to be executed by the applicant on self execution basis on payment of 5% Supervision Charges of the estimated cost.. The proposed HTVR, sketch,& other documents are enclosed for your kind reference. Hence this estimate may kindly be Sanctioned at the earliest under Self Execution by observing company formalities'
ASSISTANT EXECUTIVE ENGINEER (ELE) | [5 empty] | ASSISTANT ENGINEER (ELE)
BESCOM O&M SUB - DIVISION | [5 empty] | BESCOM SULIBELE UNIT
NANDAGUDI | [5 empty] | NANDAGUDI SUB DIVISION

## hsk AFTER
BANGALORE ELECRTICITY SUPPLY COMPANY LIMITED
HT Voltage regulation of F-9 HSK LOGISTIC Feeder Eminating from 66/11 KV SULIBELE MUSS
|  |  |  | 3.2 | [5 empty] | 0.8
[9 empty] | 3712 | 350 | KVA
PROPOSED LOAD
[5 empty] | KVA | X | KM | = | KVA KM
[5 empty] | 350 | X | 0.8 | = | 280
[5 empty] | 4062 | X | 3.2 | = | 12998.4
13278.4
| HTVR = | KVA KM X Const |  |  | = | 13278 X 0.0236
|  | DF X 100 |  |  |  | 1 X 100
|  | HTVR | = | 3.13%
Assistant Engineer(Ele) | [6 empty] | Asst.Executive Engineer (Ele)
BESCOM, Sulibele | [6 empty] | BESCOM,Nanadagudi Sub Division
Nandagudi Sub Division | [6 empty] | Nandagudi Sub Division
66/11 KV SULIBELE MUSS
3*400 SQMM UG CABLE

## Sheet2 (9)
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
( Wholly owned Government of Karnataka Undertaken )
FEASIBILITY REPORT
SUB - STATION DETAILS :
1 | NAME OF THE STATION | 66/11KV Sulibele MUSS
2 | CAPACITY | 1 X 12.5MVA + 1 X 20 MVA
3 | PEAK LOAD | 20 MWs
4 | TR BANK ON WHICH THE PROPOSED LOAD IS TO BE CATERED | TR . BANK - 2
5 | CT RATIO OF TR BANK | 800/1 Amp
6 | CABLE SIZE OF TR BANK | 400 Sqmm
7 | PEAK LOAD OF TR BANK | 505 AMPS ( 8.42 MW'S )
FEEDER DETAILS :
1 | NAME OF THE FEEDER | F-9 HSK LOGISTIC
2 | CT RATIO | 400 / 1 AMPS
3 | CABLE SIZE | 400 Sqmm
4 | PEAK LOAD | 170 Amps (2.83 MW)
5 | CONDUCTOR SIZE | 3 * 400 SQMM XLPE UG CABLE
6 | HT VOLTAGE REGULATION | 3.13 % ( CHART ENCLOSED )
TRANSFORMER
1 | LOCATION | M/S APTIV COMPONENTS INDIA PVT LTD, ( LESSOR), SITUATED AT PROPERTY NO 66, BLOCK 'F' INSIDE THE PREMISES OF HSK LOGISTICS ASSESTS INDIA PVT LTD.
2 | CAPACITY | 500 KVA
3 | CONNECTED LOAD | 350 KVA
4 | PEAK LOAD | -
5 | NO OF CIRCUITS EXISTING | -
6 | NO OF CIRCUITS PROPOSED | -
7 | LOAD IN EACH CIRCUITS | -
REMARKS : The proposed 350 kva load is feasible only after completion of 11 KV Work along with OD and VL at the Tapping Point under self execution as per the estimate.
ASSISTANT EXECUTIVE ENGINEER (ELE) |  | ASSISTANT ENGINEER (ELE)
BESCOM O&M SUB - DIVISION |  | BESCOM SULIBELE UNIT
NANDAGUDI |  | NANDAGUDI SUB DIVISION