## c19
182903
MONTH:-JUNE-2025
CONSOLIDATE MONTHLY METER READING DATA FOR STATIONS - FORMAT-1
Sl. No | Particulars Line/ Transformer/ Bank/ Feeder | CT Ratio Used / (Amps) | Energy Meter Sl No | Peak Load |  |  | Zone |  |  | BMAZ | Meter Constant in KWH. | Net Energy in KWH | Meter Em or ETV. Make | Status of meter, OK/MNR/NM
[7 empty] | Imp/Exp | READINGS
|  |  |  | MW | Date | Time |  | Present | Previous | Difference
Name of the Station:- 66/11KV KADUGODI MUSS CODE No. 1110041 | [10 empty] | AE(M) - 9448487906 No.10
66kv lines.
1 | Kadugodi-EPIP Line | 1200/1 | 12093909 | 81.3 | 10.06.2025 | 19:00 | IMP | 912912 | 904491 | 8421 | 6000 | 50526000 | L & T ETV | OK | 50.526
2 | Kadugodi-Army welfare Line EXP | 600/1 | 6675201 | 31.5 | 30.06.2025 | 7:00 | EXP | 533299 | 526243 | 7056 | 3000 | 21168000 | L & T ETV | OK | 21.168
|  |  |  | 0 | 0:00 | 0:00 | IMP | 609885 | 609885 | 0 | 3000 | 0 | L & T ETV | OK
29358000
66/11kv Transformer.
1 | T1-31.5MVA:66kv Side(HV) | 400/1 | 7502 | 26.8 | 26.06.2025 | 0.29167 | Exp | 2768802 | 2703903 | 64899 | 240 | 15575760 | Secure ETV | OK | 15.5758
2 | T2-31.5MVA:66kv Side(HV) | 400/1 | 7499 | 24.7 | 10.06.2025 | 0.79167 | Exp | 1644567 | 1587087 | 57480 | 240 | 13795200 | Secure ETV | OK | 13.7952
11kv Readings. | [11 empty] | 29370960 |  |  | 29.371
| BANK - I | 1200/1 | Q0247261 | 16.5 | 28.06.2025 | 0.79167 | Imp | 3601.768 | 3534.774 | 66.994 | 120000 | 8039280 | DLMS | OK | 8.0393
1 | F1-Naduvathi. | 400/1 | Q0247225 | 4.6 | 26.06.2025 | 0.29167 | Exp | 1992.27 | 1936.772 | 55.498 | 40000 | 2219920 | DLMS | OK | I/C | -0.02565 | F1 | 2.2199
2 | F3-Muthsandra. | 400/1 | Q0247223 | 4.3 | 27.06.2025 | 0.79167 | Exp | 1774.904 | 1737.895 | 37.009 | 40000 | 1480360 | DLMS | OK | TR1 | -0.62096 | F2 | 1.213
3 | F4-Devanagundi. | 400/1 | Q0247331 | 3 | 23.06.2025 | 7:00 | Exp | 2045.74 | 2007.866 | 37.874 | 40000 | 1514960 | DLMS | OK | TR2 | 0.2714 | F3 | 1.4804
4 | F6-Sai Garden. | 400/1 | Q0247268 | 1.8 | 03.06.2025 | 19:00 | Exp | 1205.062 | 1179.194 | 25.868 | 40000 | 1034720 | DLMS | OK | B1 | 0.53686 | F4 | 1.515
5 | F16-Varthur Kodi | 400/1 | Q0246761 | 0 | 01.06.2025 | 1:00 | Exp | 1665.643 | 1665.643 | 0 | 40000 | 0 | DLMS | OK | B1A | 0.63722 | F5 | 1.1984
6 | F-18 Vijayanagara | 400/1 | Q0247272 | 3.6 | 06.06.2025 | 0.79167 | Exp | 1998.161 | 1954.507 | 43.654 | 40000 | 1746160 | DLMS | OK | B2 | 0.45985 | F6 | 1.0347
|  |  |  | 17.3 | [7 empty] | 7996120 |  |  | B2A | -0.038142 | F7 | 1.452
| BANK - I A | 1200/1 | Q1021293 | 16.3 | 03.06.2025 | 0.79167 | Imp | 639.673 | 576.063 | 63.61 | 120000 | 7633200 | DLMS | OK | 7.6332 |  | F8 | 0.60036
7 | F2 - Kadugodi | 400/1 | Q0247315 | 3.3 | 26.06.2025 | 0.29167 | Exp | 1786.011 | 1755.687 | 30.324 | 40000 | 1212960 | DLMS | OK |  |  | F9 | 1.8264
8 | F19-Urban forest | 400/1 | Q0247310 | 1 | 09.06.2025 | 0.45833 | Exp | 1938.098 | 1926.714 | 11.384 | 40000 | 455360 | DLMS | OK |  |  | F10 | 2.4932
9 | F13-SAN Engineering | 400/1 | Q0247263 | 2.8 | 03.06.2025 | 0.79167 | Exp | 638.994 | 607.315 | 31.679 | 40000 | 1267160 | DLMS | OK |  |  | F11 | 0.00384
10 | F15-Golden Blossom | 400/1 | Q0247249 | 4.6 | 03.06.2025 | 0.79167 | Exp | 2657.28 | 2619.645 | 37.635 | 40000 | 1505400 | DLMS | OK |  |  | F12 | 1.8432
11 | F20-Nagondahalli Whitefield | 400/1 | Q0258718 | 4.6 | 04.06.2025 | 0.75 | Exp | 813.087 | 772.68 | 40.407 | 40000 | 1616280 | DLMS | OK |  |  | F13 | 1.2672
12 | F21-SUMADHURA | 400/1 | Q0603653 | 0 | 01.06.2025 | 0.041667 | Exp | 937.4 | 937.4 | 0 | 2000 | 0 | DLMS | OK |  |  | F14 | 1.844
13 | F22-Reliance JIO | 400/1 | Q0748574 | 2 | 01.06.2025 | 0.25 | Exp | 15273.6 | 14509.9 | 763.7 | 2000 | 1527400 | DLMS | OK |  |  | F15 | 1.5054
|  |  |  | 11.7 | [7 empty] | 7584560 |  |  |  |  | F16 | 0
| BANK - II | 1200/1 | Q0249460 | 18 | 24.06.2025 | 0.375 | Imp | 98.269 | 8.965 | 89.304 | 120000 | 10716480 | DLMS | OK | 10.7165 |  | F17 | 2.4482
14 | F7-Mother Dairy. | 400/1 | Q0253194 | 3 | 30.06.2025 | 0.29167 | Exp | 40.133 | 3.832 | 36.301 | 40000 | 1452040 | DLMS |  |  |  | F18 | 1.7462
15 | F8-Hagadur. | 400/1 | Q0247217 | 1.8 | 30.06.2025 | 18:00 | Exp | 2580.005 | 2564.996 | 15.009 | 40000 | 600360 | DLMS | OK |  |  | F19 | 0.45536
16 | F9-B.P.L. | 400/1 | Q0247316 | 3.1 | 5.06.2025 | 7:00 | Exp | 2445.532 | 2399.873 | 45.659 | 40000 | 1826360 | DLMS | OK |  |  | F20 | 1.6163
17 | F10-White field Ind. | 400/1 | Q0247251 | 4.1 | 06.06.2025 | 0.375 | Exp | 2965.989 | 2903.659 | 62.33 | 40000 | 2493200 | DLMS | OK |  |  | F21 | 0
18 | F12-White field Town. | 400/1 | Q0246715 | 4.8 | 27.06.2025 | 0.5 | Exp | 2821.572 | 2775.492 | 46.08 | 40000 | 1843200 | DLMS | OK |  |  | F22 | 1.5274
19 | F17-Brigade cosma | 400/1 | 17094157 | 4.3 | 12.06.2025 | 0.33333 | Exp | 28501.9 | 27277.8 | 1224.1 | 2000 | 2448200 | L & T ETV | OK
20 | F11-Station Auxilliary. | 400/1 | Q0259291 | 0.1 | 01.06.2025 | 0.041667 | Exp | 968.488 | 968.392 | 0.096 | 40000 | 3840 | DLMS | OK
|  |  |  | 21.2 | [7 empty] | 10667200
| BANK - II A | 1200/1 | Q0247280 | 7.5 | 10.06.2025 | 0.79167 | Imp | 1315.148 | 1289.804 | 25.344 | 120000 | 3041280 | DLMS | OK | 3.0413
21 | F14-Sigma Tech Park | 400/1 | Q0247382 | 5.5 | 12.06.2025 | 0.5 | Exp | 2830.567 | 2784.466 | 46.101 | 40000 | 1844040 | DLMS | OK
22 | F5-AB & T | 400/1 | 20002028 | 4.3 | 27.06.2025 | 0.79167 | Exp | 22364 | 21764.8 | 599.2 | 2000 | 1198400 | L & T ETV | OK
|  |  |  | 5.5 | [5 empty] | F.Total |  | 3042440
[10 empty] | B1+B1A+B2+B2A Total | 29430240 | 29290320
Station Auxillary. | Aux. Transformer No-1 | --- | 3690055 | --- | --- | --- |  | 21057.3 | 20678.1 | 379.2 | 10 | 3792 | GENUS | OK
1
Station Auxillary Transformer Data. |  | Capacity in KVA |  | Voltage |  |  |  | Meter Provided |  | Mtr. Accy | Mtr. Make
| Aux. Transformer 1 | 1 X 100 |  | 3*240 |  |  |  | LT Side. |  | Class-1 | L & T ETV
1
% OF ERROR :- Total of Banks - Total of feeders x 100 / Total of Banks:- 0.016%

## cf7
KARNATAKA POWER TRANSMISSION CORPORATION LTD.
MONTH: -JUNE-2025
CONSUMPTION OF 11KV FEEDERS IN HOODY TL & SS DIVISION
Sl No | Name of the Station | Sl No | Name of the Feeders | Category U/R | Feeders Comsumption in KWH | Consumption at I.F Points in KWH | Intruption during the month in Hours | [7 empty] | Remarks
[7 empty] | Line Clear |  | Load Shedding |  | Single phase |  | Faulty
[7 empty] | Nos | Dur | Nos | Dur | Nos | Dur | Nos | Dur
9 | KADUGODI |  | BANK - I |  |  | 8039280 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00
|  | 1 | F1-Nadurathi. | U | 2219920 |  | 2 | 0.013889 | 0 | 0 | 0 | 0:00 | 14 | 4:15
|  | 2 | F3-Muthsandra. | U | 1480360 |  | 1 | 0.017361 | 0 | 0 | 0 | 0:00 | 6 | 1:37
|  | 3 | F4-Devanagundi. | U | 1514960 |  | 4 | 1:31 | 0 | 0 | 0 | 0:00 | 7 | 4:19
|  | 4 | F6-Sai Garden. | U | 1034720 |  | 2 | 0.022917 | 0 | 0 | 0 | 0:00 | 8 | 1:48
|  | 5 | F16-Varthur Kodi | U | 0 |  | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0
|  | 6 | F-18-Vijayanagara | U | 1746160 |  | 1 | 0.027778 | 0 | 0 | 0 | 0:00 | 5 | 1:28
|  |  | BANK - I A |  |  | 7633200 | 1 | 0.46875 | 0 | 0 | 0 | 0:00 | 0 | 0:00
|  | 7 | F2-Kadugodi. | U | 1212960 |  | 1 | 0.017361 | 0 | 0 | 0 | 0:00 | 6 | 1:12
|  | 8 | F19-URBAN FOREST | U | 455360 |  | 1 | 0.013889 | 0 | 0 | 0 | 0:00 | 6 | 10:48
|  | 9 | F13-SAN Engineering | U | 1267160 |  | 1 | 0.027778 | 0 | 0 | 0 | 0:00 | 5 | 3:08
|  | 10 | F15-Golden Blossom | U | 1505400 |  | 1 | 0.020833 | 0 | 0 | 0 | 0:00 | 3 | 0:55
|  | 11 | F20-Nagondahalli white field | U | 1616280 |  | 0 | 0 | 0 | 0 | 0 | 0:00 | 4 | 0:52
|  | 12 | F21-SUMADHURA | U | 0 |  | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00
|  | 13 | F22-RELIANCE JIO | U | 1527400 |  | 0 | 0:00 | 0 | 0 | 0 | 0:00 | 0 | 0:00
|  |  | BANK - II |  |  | 10716480 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00
|  | 12 | F7-Mother Dairy. | U | 1452040 |  | 6 | 0.085417 | 0 | 0 | 0 | 0:00 | 9 | 3:38
|  | 13 | F8-Hagdur. | U | 600360 |  | 0 | 0 | 0 | 0 | 0 | 0:00 | 5 | 65:01
|  | 14 | F9-B.P.L. | U | 1826360 |  | 1 | 0.022917 | 0 | 0 | 0 | 0:00 | 11 | 4:15
|  | 15 | F10-White field Ind. | U | 2493200 |  | 0 | 0 | 0 | 0 | 0 | 0:00 | 20 | 7:18
|  | 16 | F12-White field Town. | U | 1843200 |  | 1 | 0.013889 | 0 | 0 | 0 | 0:00 | 4 | 1:08
|  | 17 | F17-Briged cosma | U | 2448200 |  | 1 | 0.027778 | 0 | 0 | 0 | 0:00 | 5 | 0.028472
|  | 18 | F11-Station Auxillary. | U | 3840 |  | 1 | 0.0069444 | 0 | 0 | 0 | 0:00 | 1 | 0:10
|  |  | BANK - II A |  |  | 3041280 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00
|  | 19 | F14-Sigma Tech Park | U | 1844040 |  | 0 | 0 | 0 | 0 | 0 | 0:00 | 2 | 0.025
|  | 20 | F5-A.B.T. | U | 1198400 |  | 0 | 0:00 | 0 | 0 | 0 | 0:00 | 10 | 1:30
|  |  | BANK - I & II |  | 29290320 | 29430240
TOTAL

## 11kV Bank & Feeder interruption
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED.
JUNE-2025
Sl No | Name of the Station | Sl No | Name of the feeders | EFR |  | OCR |  | EFR & OCR |  | Major Break Downs |  | Unscheduled |  |  |  | Hand Trip |  | Line Clear |  | Load Shedding |  | Scheduled |  | Un-Scheduled |  | Remarks
FAULTY
|  |  |  | Nos | Dur | Nos | Dur | Nos | Dur | Nos | Dur | Nos | Dur | Nos. | Dur | Nos | Dur | Nos | Dur | Nos | Dur | Nos | Dur | Nos | Dur |  | Nos | Dur
11 | 66/11KV Kadugodi. |  | BANK I | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0 | 0 | 0
|  | 1 | F1-Naduvathi | 6 | 0.03125 | 0 | 0 | 8 | 0.14583 | 0 | 0:00 | 0 | 0:00 | 14 | 4:15 | 0 | 0 | 2 | 0.013889 | 0 | 0 | 2 | 0:20 | 14 | 4:15 |  | 14 | 0.17708 | 16 | 0.19097
|  | 2 | F3-Muthsandra | 5 | 0.056944 | 1 | 0.010417 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 6 | 1:37 | 0 | 0 | 1 | 0.017361 | 0 | 0 | 1 | 0:25 | 6 | 1:37 |  | 6 | 0.067361 | 7 | 0.084722
|  | 3 | F4-Devanagundi | 4 | 0.033333 | 1 | 0:05 | 2 | 0.14306 | 0 | 0:00 | 0 | 0:00 | 7 | 4:19 | 0 | 0 | 4 | 0.063194 | 0 | 0 | 4 | 1:31 | 7 | 4:19 |  | 7 | 0.17986 | 11 | 0.24306
|  | 4 | F6-Sai Garden | 3 | 0.015278 | 3 | 0.024306 | 2 | 0.035417 | 0 | 0:00 | 0 | 0:00 | 8 | 1:48 | 0 | 0 | 2 | 0.022917 | 0 | 0 | 2 | 0:33 | 8 | 1:48 |  | 8 | 0.075 | 10 | 0.097917
|  | 5 | F16-Varthur Kodi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | 6 | F-18-Vijayanagara | 4 | 0.036111 | 0 | 0 | 1 | 0.025 | 0 | 0:00 | 0 | 0:00 | 5 | 1:28 | 0 | 0 | 1 | 0.027778 | 0 | 0 | 5 | 0:40 | 5 | 1:28 |  | 5 | 0.061111 | 10 | 0.088889
|  |  | BANK - I A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0 | 1 | 0.46875 | 0 | 0 | 1 | 11:15 | 0 | 0:00 |  | 0 | 0 | 1 | 0.46875
|  | 7 | F2 - Kadugodi | 5 | 0:34 | 0 | 0 | 1 | 0.026389 | 0 | 0:00 | 0 | 0:00 | 6 | 1:12 | 0 | 0 | 1 | 0.017361 | 0 | 0 | 1 | 0:25 | 6 | 1:12 |  | 6 | 0.05 | 7 | 0.067361
|  | 8 | F19-URBAN FOREST | 2 | 0:15 | 0 | 0 | 4 | 10:33 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0 | 1 | 0:20 | 0 | 0 | 1 | 0:20 | 6 | 10:48 |  | 6 | 0.45 | 7 | 0.46389
|  | 9 | F13-SAN Engineering | 1 | 0.0125 | 1 | 0.013194 | 3 | 0.10486 | 0 | 0:00 | 0 | 0:00 | 5 | 3:08 | 0 | 0 | 1 | 0.027778 | 0 | 0 | 1 | 0:40 | 5 | 3:08 |  | 5 | 0.13056 | 6 | 0.15833
|  | 10 | F15-Golden Blossom | 1 | 0.0034722 | 1 | 0.0069444 | 1 | 0.027778 | 0 | 0:00 | 0 | 0:00 | 3 | 0:55 | 0 | 0 | 1 | 0.020833 | 0 | 0 | 1 | 0:30 | 3 | 0:55 |  | 3 | 0.038194 | 4 | 0.059028
|  | 11 | F20-Nagondahalli white field | 4 | 0.036111 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 4 | 0:52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0:00 | 4 | 0:52 |  | 4 | 0.036111 | 4 | 0.036111
|  | 12 | F21-SUMADHURA | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0 | 0 | 0
|  | 13 | F22-RELIANCE JIO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0 | 0 | 0
|  |  | BANK - II | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0 | 0 | 0
|  | 14 | F7-Mother Dairy. | 2 | 0.034028 | 6 | 0.093056 | 1 | 0.024306 | 0 | 0:00 | 0 | 0:00 | 9 | 3:38 | 0 | 0:00 | 6 | 0.085417 | 0 | 0 | 6 | 2:03 | 9 | 3:38 |  | 9 | 0.15139 | 15 | 0.23681
|  | 15 | F8-Hagdur. | 5 | 2.709 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 5 | 65:01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0:00 | 5 | 65:01 |  | 5 | 1900-01-01 17:01 | 5 | 1900-01-01 17:01
|  | 16 | F9-B.P.L. | 9 | 0.085417 | 0 | 0 | 2 | 0.091667 | 0 | 0:00 | 0 | 0:00 | 11 | 4:15 | 0 | 0 | 1 | 0.022917 | 0 | 0 | 1 | 0:33 | 11 | 4:15 |  | 11 | 0.17708 | 12 | 0.2
|  | 17 | F10-White field Ind. | 7 | 2:08 | 4 | 0.061806 | 9 | 0.15347 | 0 | 0:00 | 0 | 0:00 | 20 | 7:18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0:00 | 20 | 7:18 |  | 20 | 0.30417 | 20 | 0.30417
|  | 18 | F12-White field Town. | 1 | 0.027778 | 2 | 0.013889 | 1 | 0.0055556 | 0 | 0:00 | 0 | 0:00 | 4 | 1:08 | 0 | 0 | 1 | 0.013889 | 0 | 0 | 1 | 0:20 | 4 | 1:08 |  | 4 | 0.047222 | 5 | 0.061111
|  | 19 | F17-Briged cosmapoles | 3 | 0:33 | 0 | 0 | 2 | 0.0055556 | 0 | 0:00 | 0 | 0:00 | 5 | 0:41 | 0 | 0 | 1 | 0.027778 | 0 | 0 | 1 | 0:40 | 5 | 0:41 |  | 5 | 0.028472 | 6 | 0.05625
|  | 20 | F11-Station Auxillary. | 1 | 0.0069444 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 1 | 0:10 | 0 | 0 | 1 | 0.0069444 | 0 | 0 | 1 | 0:10 | 1 | 0:10 |  | 1 | 0.0069444 | 2 | 0.013889
|  |  | BANK - II A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00 |  | 0 | 0 | 0 | 0
|  | 21 | F14-Sigma Tech Park | 2 | 0.025 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 2 | 0:36 | 0 | 0 | 0 | 0:00 | 0 | 0 | 0 | 0:00 | 2 | 0.025 |  | 2 | 0.025 | 2 | 0.025
|  | 22 | F5-A.B.T. | 10 | 0.0625 | 0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0:00 | 10 | 1:30 | 0 | 0 | 0 | 0:00 | 0 | 0 | 0 | 0:00 | 10 | 1:30 |  | 10 | 0.0625 | 10 | 0.0625
Formulas:
Dur = [Dur]+[Dur]+[Dur]

## Tr. Peak load
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
(Cons) PEAKLOAD DETAILS PERTAINS TO HOODY DIVISION. MONTH:-JUNE-2025
Sl No | Name of the Station. | Transformer Ratio in KV. | Transformer Capacity in MVA. | Total MVA. | Peak Load in MW. | Peak Load in Amps. Primary-Side. | Date. | Time | Percentage of Loading.
10 | 66/11kv Kadugodi. | TR:1:-66 / 11 | 31.5 | 63 | 26.8 | 268 | 26.06.2025 | 0.29167 | 85.0794
|  | TR:2:-66 / 11 | 31.5 |  | 24.7 | 247 | 10.06.2025 | 0.79167 | 78.4127
BANK-1A LC 10:30 TO 21:45=11:15 (DUE TO BANK-1A "Y" PHASE POTHEAD & 11KV PT REPLACEMENT

## Lines peak
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED.
MONTH:-JUNE-2025
(CONS) FORMAT 2 (Pertains to Hoody TL & SS Division).
Sl No | Name of the Station | Name of the Lines | Maximum peak load |  |  |  |  | No. of Interruptions |  |  |  | Energy Sent out in KWH
|  |  | Recorded during the month |  |  |  |  | Forseen |  | Unforseen
|  |  | MW | Amps | Date | Time | MVAR | Nos | Hrs | Nos | Hrs | Import | Export
1 | 66/11KV Kadugodi. | Kadugodi-EPIP Line | 81.3 | 813 | 10.06.2025 | 19:00 |  | 0 | 0:00 | 1 | 0:50 | 50526000 | 0
|  | Kadugodi-Army welfare | 31.5 | 315 | 30.06.2025 | 7:00 |  | 0 | 0:00 | 0 | 0:00 | 0:00 | 21168000
| I/C LINE | [5 empty] | O/G LINE
MAIN SUPPLY FAILURE AT EPIP 220KV STATION 27.06.2025 0:58 TO 1:48=0:50MIN

## R-Index
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED.
MONTH:-JUNE-2025
RELIABILITY INDEX
SL. NO. | Name of the Station | voltage class | T | N | T-N | Reliability T-N / T X 100 | Remarks
9 | 66/11KV KADUGODI. | 66/11kV | 1900-01-29 | 0.034722 | 1900-01-28 23:10 | 99.88% | MAIN SUPPLY FAILURE AT EPIP 220KV STATION 27.06.2025 0:58 TO 1:48=0:50MIN
Formulas:
T-N = [T]-[N]

## Stn. peak
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED.
MONTH=JUNE-2025
(CONS) FORMAT 1 (Pertains to Hoody TL & SS Division)
Sl No | Name of the station | Tr. In MVA | Max Peak Load Recorded During the month |  |  |  |  | Max Voltage Recorded in KV | [5 empty] | Min Voltage Recorded in KV | [5 empty] | Received from I.P.P.S |  | Energy sent out from MUSS in KWH
|  |  | MW | Amps | Date | Time In Hrs | MVAR | HV/KV | Date | Time In Hrs | LV/ KV | Date | Time In Hrs | HV/KV | Date | Time In Hrs | LV/ KV | Date |  | 11KV (Max) | EHV (Min)
10 | 66/11KV Kadugodi. | 63 | 51.1 | 511 | 10.06.2025 | 0.79167 | _ | 66 | 01.06.2025 | 0.041667 | 11 | 01.06.2025 | 0.041667 | 65 | 01.06.2025 | 0.29167 | 10.8 | 03.06.2025 | 0.25 | --- | --- | 29370960

## B FORMS OF IF POINT
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
B-Forms of IF Points
Name of the Station: Kadugodi | [8 empty] | IF point Sl No:
Name of the Division: TL-SS Division Hoody | [8 empty] | Month: | JUNE-2025
Sl. No. | Sub-Station Name | Interface Point | Meter Type | CT Ratio | Meter SL No. | Flow Type | MF | Initial | Final | Consumption | Remarks
1 | Kadugodi | 66/11 KV BANK-1 | DLMS | 1200/1 | Q0247261 | Import | 120000 | 3534.774 | 3601.768 | 8039280
|  | 66/11 KV BANK-1A | DLMS | 1200/1 | Q1021293 | Import | 120000 | 576.063 | 639.673 | 7633200
3 |  | 66/11 KV BANK-2 | DLMS | 1200/1 | Q0249460 | Import | 120000 | 8.965 | 98.269 | 10716480
4 |  | 66/11 KV BANK-2A | DLMS | 1200/1 | Q0247280 | Import | 120000 | 1289.804 | 1315.148 | 3041280
5 |  | AUX | GENUS | --- | 3690055 | Export | 10 | 20678.1 | 21057.3 | 3792
6 |  | EHT | --- | --- | --- | --- | --- | --- | --- | ---
7 |  | IPP | --- | --- | --- | From KPTCL | --- | --- | --- | ---
|  | IPP | --- | --- | --- | To KPTCL | --- | --- | --- | ---
29434032
Annexure
Sl. No. | Sub-Station Name | Interface Point | Meter Type | CT Ratio | Meter SL No. | Flow Type | MF | Initial | Final | Consumption | Remarks
1 | Kadugodi | Transformer-1 | Secure ETV | 400/1 | 7502 | Export | 240 | 2703903 | 2768802 | 15575760
2 |  | Transformer-2 | Secure ETV | 400/1 | 7499 | Export | 240 | 1587087 | 1644567 | 13795200
[10 empty] | 29370960 | -0.21474
| Asst Engineer (Ele) |  | Asst Executive Engineer (Ele) |  |  |  |  | Executive Engineer (Ele)
| 66/11 KV Kadugodi |  | Nodal Officer |  |  |  |  | TL&SS Division

## 66KV TRANSFORMERS
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED
Availability for the month of :-JUNE-2025
NAME OF THE CIRCLE: BMAZ South Circle
NAME OF THE ELEMENT: 66KV TRANSFORMERS
Sl No | Name of the Transformer | Voltage level in K.V | Capacity in MVA | Weightage factor=MVA Capacity | Total Time in Hours | Un-Schedule interruption in Hours | Availabilty index | Availability | %ge availability | Reason
1 | Kadugodi MUSS Tr - 1 31.5MVA | 66 / 11 | 31.5 | 31.5 | 1900-01-29 | 0.36458 | 0.37153 | 11.7031 | 37.1528 | (1) TRANSFORMER-1 TRIPPED ON OCR A,B,C PHASE DIFFERENTIAL RELAY A,B,C PHASE EFR &TRIP 86 MASTER RELAY BANK-1A "Y" PHASE CABLE POTHEAD & 11KV PT FLASH OVER 27.06.2025 00:58 TO 1:48=0:50 MIN (2) TRANSFORMER-1 LC (DUE TO BANK1A CABLE REMOVING WORK) 27.06.2025 01:58 TO 4:20=2:22 HRS (3) TRANSFORMER-1 LC (DUE TO BANK1A CABLE REMOVING WORK) 27.06.2025 06:45 TO 10:30=3:45 HRS (4) TRANSFORMER-1 LC (DUE TO BANK1A CABLE CONNECTING WORK) 27.06.2025 20:35 TO 21:48=1:48 HRS TOTAL:-8:55 HRS
2 | Kadugodi MUSS Tr - 2 31.5MVA | 66 / 11 | 31.5 | 31.5 | 1900-01-29 | 0.048611 | 0.99838 | 31.449 | 99.838 | (1) TRANSFORMER-2 LC (DUE TO BANK2A CABLE REMOVING WORK) 27.06.2025 01:58 TO 2:34=0:36 HRS (2) TRANSFORMER-1 LC (DUE TO BANK1A CABLE CONNECTING WORK) 27.06.2025 08:55 TO 9:29=0:34 HRS TOTAL:-01:10 HRS
Superintending Engineer (Elec.),
Trans. (Maint), BMAZ South, KPTCL
Bangalore.