## Input Energy
Sub Division wise AT&C and T&D loss Abstract for the month of | [7 empty] | July-25 INPUT and August-25 DCB
Energy Audit of Feeders |  | July-25 INPUT and August-25 DCB |  |  | of Kyatsandra Sub Division
Name of the Sub Division | Total No of Feeders | Input Energy in Units (Feeder Consumption) | Station Auxiliary consumption in Units | Import Energy in Units | Export Energy in Units | EHT Consumption in Units | 11KV Wheeled Energy in Units (Input) | Above 11KV Wheeled Energy in Units (Input) | 11KV Open Acess in Units (input) | Above 11KV Open Acess in Units (input) | 11KV IPP in Units (input) | Above 11KV IPP in Units (input) | SRTPV (Net Metering + Gross Metering) in Units | Net Input Energy in MU (Input+Import-Export+ EHT+ SRTPV) | Metered Sales in Units as per DCB | EHT Consumption in Units (Sales as per DCB) (It should not be added in the metered sales) | 11KV Wheeled Energy in Units (Sales as per DCB) (It should not be added in the metered sales) | Above 11KV Wheeled Energy in Units (Sales as per DCB) (It should not be added in the metered sales) | 11KV Open Acess in Units (sales as per DCB) (It should not be added in the metered sales) | Above 11KV Open Acess in Units (sales as per DCB) (It should not be added in the metered sales) | Un-Metered Sales in Units | Station Auxiliary consumption in Mus | Total Energy Sold in Units | Loss of Energy in Units | % Distribution Loss | Billing Efficiency % | Demand in Rs | Collection in Rs | Collection efficiency % | % AT&C Loss | AT&C Loss in Units = ATC Loss in % * Input Energy | ARR | Loss in Amount (Rs) =ARR*AT&C Loss in Units
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15=3+4+5-6+7+9+11+14 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24=16+17+18+19+20+21+22+23 | 25=15-24 | 26=25/15*100 | 27=24/15 | 28 | 29 | 30=29/28 | 31=(1-(27*30)/10000)*100 | 32=(31/100)*15 | 33=28/(24*1000000) | 34=33*32
Kyathsandra | 52 | 19814760 | 6174.5 | 4864525 | 3482820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2520 | 21205159.5 | 10553229.75 | 0 | 2961799 | 0 | 0 | 0 | 6086873.709 | 6174.5 | 19608076.959 | 1597082.541 | 7.5316 | 92.4684 | 163807255.04 | 158878625.94 | 96.9912 | 10.3138 | 2187049.9309 | 8.3541 | 18270769.059
Sub Division wise AT&C and T&D loss Abstract for the month of
Energy Audit of Feeders
Name of the Sub Division | Total No of Feeders | Input Energy in MUs (Feeder Consumption) | Station Auxiliary consumption in MUs | Import Energy in MUs | Export Energy in MUs | EHT Consumption in MUs | 11KV Wheeled Energy in MUs (Input) | Above 11KV Wheeled Energy in MUs (Input) | 11KV Open Acess in MUs (input) | Above 11KV Open Acess in MUs (input) | 11KV IPP in MUs (input) | Above 11KV IPP in MUs (input) | SRTPV (Net Metering + Gross Metering) in MUs | Net Input Energy in MU (Input+Import-Export+ EHT+ SRTPV) | Metered Sales in MUs as per DCB | EHT Consumption in MUs (Sales as per DCB) (It should not be added in the metered sales) | 11KV Wheeled Energy in MUs (Sales as per DCB) (It should not be added in the metered sales) | Above 11KV Wheeled Energy in MUs (Sales as per DCB) (It should not be added in the metered sales) | 11KV Open Acess in MUs (sales as per DCB) (It should not be added in the metered sales) | Above 11KV Open Acess in MUs (sales as per DCB) (It should not be added in the metered sales) | Un-Metered Sales in MUs | Station Auxiliary consumption in Mus | Total Energy Sold in MUs | Loss of Energy in MUs | % Distribution Loss | Billing Efficiency % | Demand in Rs | Collection in Rs | Collection efficiency % | % AT&C Loss | AT&C Loss in MUs = ATC Loss in % * Input Energy | ARR | Loss in Amount (Rs) =ARR*AT&C Loss in MUs
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15=3+4+5-6+7+9+11+12+13+14 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24=16+17+18+19+20+21+22+23 | 25=15-24 | 26=25/15*100 | 27=24/15 | 28 | 29 | 30=29/28 | 31=(1-(27*30)/10000)*100 | 32=(31/100)*15 | 33=28/(24*1000000) | 34=33*32
Kyathsandra | 52 | 19.8148 | 0.0061745 | 4.8645 | 3.4828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00252 | 21.2052 | 10.5532 | 0 | 2.9618 | 0 | 0 | 0 | 6.0869 | 0.0061745 | 19.6081 | 1.5971 | 7.5316 | 92.4684 | 163807255.04 | 158878625.94 | 96.9912 | 10.3138 | 2187049.9309 | 8.3541 | 18270769.059

## Feeder Details
Energy Audit of Feeders for the month of | [7 empty] | July-25 INPUT and August-25 DCB
Feeder Details | [6 empty] | of Kyatsandra Sub Division
Division Sl No | Sub Division Sl No | Sub Division / Division | Feeder Owner (Sub Division) | STATION | FEEDER NO.& NAME (as per MDM) | FEEDER CODE (as per MDM) | Type of Feeder as per MDM | 100% Feeding to SD (Y/N) | Shared with |  |  |  | Boundary Meter provided (Y/N) | If not provided, % of sharing |  |  | Boundary Meter details |  |  | Remarks-for not providing Boundary meter
[9 empty] | Sub Division | Division | Circle | Zone |  | SD1 | SD2 | SD3 | Make | CT Ratio | Constant
1 | 1 | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F08-BADDIHALLI | 1320105901020300 | MIXED LOAD | Y
2 | 2 | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F10-CM-EXTENSION | 1320105901020300 | NJY | Y
3 | 3 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F09-MARNAYAKANAPALYA | 1320105902020300 | MIXED LOAD | Y
4 | 4 | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F09-KESARAMODU-NJY | 1320105901020300 | AGRI | Y
5 | 5 | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F11-KALAHALLI | 1320105901020300 | AGRI | Y
6 | 6 | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F12-KESARAMODU | 1320105901020300 | INDUSTRIAL | Y
7 | 7 | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F14-SKS | 1320105901020300 | DOMESTIC | Y
8 | 8 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F01-CIPSA | 1320105902010100 | AGRI | Y
9 | 9 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F03-HARALURU | 1320105902010100 | MIXED LOAD | Y
10 | 10 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F04-INCAP | 1320105902010100 | INDUSTRIAL | Y
11 | 11 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F05-INDUSTRIAL | 1320105902010100 | AGRI | Y
12 | 12 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F06-K-M-HALLI | 1320105902020300 | INDUSTRIAL | Y
13 | 13 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F07-CARMOBILES | 1320105902020300 | AGRI | N | DOBASPETE | NELAMANGALA | BANGALORE NORTH | BRAZ | N | 12%
14 | 14 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F08-HIREHALLI | 1320105902020300 | DOMESTIC | Y
15 | 15 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F10-SIDDAGANGA-MATA | 1320105902020300 | DOMESTIC | Y
16 | 16 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F11-RAITHARAPALYA | 1320105902020300 | NJY | Y
17 | 17 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F12-NANDIHALLI-NJY | 1320105902010100 | NJY | N | DOBASPETE | NELAMANGALA | BANGALORE NORTH | BRAZ | N | 25%
18 | 18 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F14-RANE WALES | 1320105902010100 | INDUSTRIAL | Y
19 | 19 | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F15-KOLIHALLI | 1320105902020300 | AGRI | Y
20 | 20 | KYATSANDRA | TUMKUR RURAL SUB DIVISION2 | HONNENAHALLI_66 | F03-KARENAHALLI IP | 1320104906010100 | AGRI | Y
21 | 21 | KYATSANDRA | TUMKUR RURAL SUB DIVISION2 | HONNENAHALLI_66 | F04-HONASIGERE IP | 1320104906010100 | AGRI | Y
22 | 22 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F01-THAVAREKERE | 1320105903010100 | AGRI | Y
23 | 23 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F02-MULUKUNTE | 1320105903010100 | AGRI | Y
24 | 24 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F03-HONNUDIKE | 1320105903010100 | AGRI | Y
25 | 25 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F04-SASALU | 1320105903010100 | AGRI | Y
26 | 26 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F05-HOLAKALLU | 1320105903010100 | AGRI | N
27 | 27 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F06-CHOLAMBALLI | 1320105903020300 | AGRI | Y
28 | 28 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F07-VIRUPASANDRA | 1320105903020300 | AGRI | Y | RSD2 | TUMKUR | TUMKUR | CTAZ | N | 40%
29 | 29 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F08-HONNUDIKE-NJY | 1320105903020300 | NJY | Y
30 | 30 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F09-CNNL | 1320105903020300 | WATER WORKS | Y
31 | 31 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F10-HOLAKALLU-NJY | 1320105903020300 | NJY | N | CSD2 & RSD2 | TUMKUR | TUMKUR | CTAZ | N | 32% | 10% |  |  |  |  | Boundary metering work is under progress
32 | 32 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F11-ARENAHALLI | 1320105903020306 | NJY | Y
33 | 33 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F12-MAASKAL | 1320105903020307 | NJY | Y
34 | 34 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F13-VAHINI PIPES | 1320105903010300 | INDUSTRIAL | Y
35 | 35 | KYATSANDRA | KYATSANDRA | HONNUDIKE_66 | F14-JOLUMARANAHALLI | 1320105903020300 | AGRI | Y
36 | 36 | KYATSANDRA | KYATSANDRA | URDIGERE_66 | F01-SEETHAKALLU | 1320105904010100 | AGRI | Y
37 | 37 | KYATSANDRA | KYATSANDRA | URDIGERE_66 | F02-MYDALA | 1320105904010100 | NJY | Y
38 | 38 | KYATSANDRA | KYATSANDRA | URDIGERE_66 | F03-D.DURGA | 1320105904010100 | AGRI | Y
39 | 39 | KYATSANDRA | KYATSANDRA | URDIGERE_66 | F04-URDIGERE-RURAL | 1320105904010100 | AGRI | Y
40 | 40 | KYATSANDRA | KYATSANDRA | URDIGERE_66 | F05-KALENAHALLI | 1320105904020300 | NJY | Y
41 | 41 | KYATSANDRA | KYATSANDRA | URDIGERE_66 | F06-KURUVELU | 1320105904020300 | AGRI | Y
42 | 42 | KYATSANDRA | KYATSANDRA | URDIGERE_66 | F07-SATHAGHATTA | 1320105904020300 | NJY | Y
43 | 43 | KYATSANDRA | KYATSANDRA | URDIGERE_66 | F08-HALUGONDANAHALLI | 1320105904010100 | AGRI | Y
44 | 44 | KYATSANDRA | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | F15-NIDUVALALU -NJY | 1320104903020500 | NJY | N | RSD2 | TUMKUR | TUMKUR | CTAZ | N | 20%
45 | 45 | KYATSANDRA | TUMKUR RURAL SUB DIVISION2 | HONNENAHALLI_66 | F02-HONNENAHALLI IP | 1320104906010100 | AGRI | N | RSD2 | TUMKUR | TUMKUR | CTAZ | N | 40%

## T&D Loss Abstract
Energy Audit of Feeders for the month of | [8 empty] | July-25 INPUT and August-25 DCB
Energy Audit of Feeders for the month of | [7 empty] | July-25 INPUT and August-25 DCB |  |  |  | of Kyatsandra Sub Division
Sub Division / Division | Total No. of Feeders | No. of Feeders audited | Loss Range |  |  |  |  | No. of Feeders Not audited | Reasons for feeders with -ve, >10% loss and Not audited | [5 empty] | REMARKS
|  |  | Negative | >0 to< 5% | > 5% to < 10% | > 10 to < 15% | > 15 % |  | Reasons For Industrial feeders -ve and >10% | Reasons For Urban feeders -ve and >10% | Reasons For NJY feeders -ve and >10% | Reasons For Mixed Load feeder -ve and >12% | Reasons For Other feeders -ve and >15% | Reasons Not Audited
KYATSANDRA | 52 | 52 | 3 | 2 | 47 | 0 | 0 | 0 | All are dedicated Feeders | NIL | NIL | NIL | NIL | NIL

## AT&C Loss Abstract
Energy Audit of Feeders for the month of July-25 INPUT and August-25 DCB
Energy Audit of Feeders July-25 INPUT and August-25 DCB of Kyathsandra Sub Division
Sub Division / Division | Total No. of Feeders | No. of Feeders audited | AT & C Loss Range |  |  |  |  | No. of Feeders Not audited | Reasons for 10% loss and Not audited
|  |  | Negative | >0 to< 5% | > 5% to < 10% | > 10 to < 15% | > 15 % |  | Reason For -ve loss | Reason For >15% loss
KYATSANDRA | 52 | 52 | 4 | 2 | 20 | 12 | 14 | 0 | Collection efficiency is high | Due to poor Collection Efficiency

## Feederwise Energy Audit
Feeder to Consumer Audit |  |  | July-25 INPUT and August-25 DCB
SL. No. | AREA- RAPDRP/Non_RAPDRP/sharing between RAPDRP & Non_RAPDRP | Sub Division | O&M Section | STATION | FEEDER NO.& NAME (as per MDM) | FEEDER CODE (as per MDM) | Feeder Type CATEGORY-Urban/ Rural/ Industrial/ Commercial/ Domestic/ NJY/ AGRI/ Mixed Load/ Water works/ others | Length of the Feeder in Km |  |  | Total No of DTCs on Feeder | Total Installation Counts |  | FEEDER METER READING DETAILS | [6 empty] | BOUNDARY METER READING DETAILS | [11 empty] | 11 KV Wheeled Energy in Units | 11KV OPEN ACCESS Consumption in Units (Input) | SRTPV (Net Metering + Gross Metering) | TOTAL INPUT ENERGY (FEEDER CONSUMPTION + IMPORT-EXPORT+SRTPV) in Units | 11KV OPEN ACCESS Consumption in Units (Sales) (It should not be added in the metered sales) | 11KV Wheeled Energy in Units (Sales) (It should not be added in the metered sales) | BILLED CONSUMPTION (Metered Sales) in Units | Unmetered consumption (LT4a/ SL/ WS) in Units | TOTAL ENERGY SALES in Units | Sales as per T&D Loss Report | Energy Loss in Units | %feeder Loss | T&D Loss Range |  | %Billing Efficiency | % BE with Assessed Sales | OB | Demand In Rs | Collection In Rs | CB | % Collection Efficiency | %AT&C loss | % AT & C LOSS with BE assessed | AT&C Loss Range 1 | Collection Efficiency restricted to 100% | % AT & C LOSS CE restricted to 100% | AT&C Loss Range-2 | Assessed Sales in Units | TOTAL Sales after assessment | Anaylized Feeder loss after assessing the energy | T&D Loss Range after assessment | Remarks (Assessed Energy/ Import/ Export/Others) | REMARKS & Reasons for -ve, above 10% for T & D LOSS | REMARKS & Reasons for-ve above 10% for AT&C LOSS | Action Plan for reducing the T&D LOSS | Methodology adopted to achieve T&Dloss below 3% | REMARKS & Reasons for-ve above 10% for AT&C LOSS
[14 empty] | FR | IR | DIFF | METER CONSTANT | FEEDER CONSUMPTION IN UNITS | CORRECTION FACTOR | FEEDER CONSUMPTION WITH CF IN UNITS | IMPORT |  |  |  | Import (Change over feeder/ Assessed where no boundary meter) | TOTAL IMPORT IN UNITS | EXPORT |  |  |  | Export (Change over feerder/Accessd where no boundary meter) | TOTAL EXPORT IN UNITS
[8 empty] | Trunk Line | Spur Line | Total Length |  | Other than LT4a | LT4a | [7 empty] | FR | IR | DIFF | CONSTANT |  |  | FR | IR | DIFF | CONSTANT
1 | 1a | 2 | 3 | 4 | 5 | 6 | 7 | 7a | 7b | 7c | 8 | 9 | 10 | 11 | 12 | 13=11-12 | 14 | 15=13*14 | 16 | 17 | 18 | 19 | 20=18-19 | A | B | 21=(20*A)+B | 22 | 23 | 24=22-23 | C | D | 25=(24*C)+D | 26 | 27 | 28 | 29=17+21-25+28 | 30 | 31 | 32 | 33 | 34=30+31+ 32+33 |  | 35=29-34 | 36=35/29*100 |  |  | 37=34/29*100 | 38=49/29*100 | 39 | 40 | 41 | 42 | 43=41/40*100 | 44=(1-(37*43)/ 10000)*100 | 45=((1-38*43/10000))*100 |  | 46 | 47=((1-38*46/10000))*100 |  | 48 | 49=34+48 | 50=(29-49)/29*100 |  | 47 | 48 |  |  |  | 49
1 | RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F08-BADDIHALLI | 1320105901020300 | MIXED LOAD | 6.4 | 13.81 | 20.21 | 92 | 7815 | 7 | 2271.322 | 2226.661 | 44.661 | 20000 | 893220 | 1 | 893220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 893220 |  | 0 | 772216.09 | 31865.32 | 804081.41 |  | 89138.59 | 9.9795 | 5-10 | 9.46 | 90.0205 | 90.0205 | 3439519.56 | 7886566.67 | 7539092.85 | 3786373.38 | 95.5941 | 13.9457 | 13.9457 | 10-15 | 95.5941 | 13.9457 | 10-15 |  | 804081.41 | 9.9795 | 5-10
2 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F09-KESARAMODU-NJY | 1320105901020300 | NJY | 8.4 | 4.6 | 13 | 67 | 2383 | 0 | 1976.441 | 1937.143 | 39.298 | 20000 | 785960 | 1 | 785960 | 0 | 0 | 0 | 0 | 70000 | 70000 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2520 | 858480 |  | 0 | 788636 | 0 | 788636 | 788636 | 69844 | 8.1358 | 5-10 | 8.14 | 91.8642 | 91.8642 | 11940282.82 | 8431243.28 | 10215264.64 | 10156261.46 | 121.1596 | -11.3024 | -11.3024 | <0 | 100 | 8.1358 | 5-10 |  | 788636 | 8.1358 | 5-10 | Import from F04-INCAP feeder due to load changeover
3 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F10-CM-EXTENSION | 1320105901020300 | MIXED LOAD | 16 | 6.5 | 22.5 | 111 | 412 | 0 | 2129.246 | 2086.776 | 42.47 | 20000 | 849400 | 1 | 849400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766000 | 766000 |  |  |  | 83400 |  | 0 | 76185 | 0 | 76185 | 76185 | 7215 | 8.6511 | 5-10 | 8.65 | 91.3489 | 91.3489 | 543466.7 | 1069887.45 | 992963.15 | 620391 | 92.8101 | 15.219 | 15.219 | 15-20 | 92.8101 | 15.219 | 15-20 |  | 76185 | 8.6511 | 5-10 | Export to RAPDRP Area of F10-CM-EXTENSION
| RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F10-CM-EXTENSION | 1320105901020300 | MIXED LOAD |  |  |  |  | 7985 | 6 |  |  | 0 |  | 0 | 1 | 0 |  |  |  | 0 | 766000 | 766000 |  |  |  |  | 0 | 0 |  |  |  | 766000 |  | 0 | 677114.7 | 13788 | 690902.7 |  | 75097.3 | 9.8038 | 5-10 | 8.65 | 90.1962 | 90.1962 | 3257680.09 | 6827409.2 | 6446094.41 | 3635927.88 | 94.4149 | 14.8413 | 14.8413 | 10-15 | 94.4149 | 14.8413 | 10-15 |  | 690902.7 | 9.8038 | 5-10 | Import from RAPDRP Area of F10-CM-EXTENSION
4 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F11-KALAHALLI | 1320105901020300 | AGRI | 7.5 | 3.5 | 11 | 47 | 56 | 275 | 718.278 | 708.598 | 9.68 | 20000 | 193600 | 1 | 193600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 193600 |  | 0 | 21742 | 153273.271 | 175015.271 | 174918.411 | 18584.729 | 9.5996 | 5-10 | 9.65 | 90.4004 | 90.4004 | 4653674.1 | 1542019.93 | 1400245.93 | 4795448.1 | 90.806 | 17.911 | 17.911 | 15-20 | 90.806 | 17.911 | 15-20 |  | 175015.271 | 9.5996 | 5-10
5 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F12-KESARAMODU | 1320105901020300 | AGRI | 1.8 | 0 | 1.8 | 47 | 4 | 342 | 850.959 | 840.437 | 10.522 | 20000 | 210440 | 1 | 210440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 210440 |  | 0 | 332 | 190913.377 | 191245.377 | 190131.057 | 19194.623 | 9.1212 | 5-10 | 9.65 | 90.8788 | 90.8788 | 494877.28 | 1721883.42 | 1719533.42 | 497227.28 | 99.8635 | 9.2452 | 9.2452 | 5-10 | 99.8635 | 9.2452 | 5-10 |  | 191245.377 | 9.1212 | 5-10
6 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F14-SKS | 1320105901020300 | DOMESTIC |  |  |  | 1 | 117 | 5 | 770.631 | 735.278 | 35.353 | 20000 | 707060 | 1 | 707060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626000 | 626000 |  |  |  | 81060 |  | 0 | 74928 | 3990.95 | 78918.95 | 78918.95 | 2141.05 | 2.6413 | 0-5 | 2.64 | 97.3587 | 97.3587 | 1734988.55 | 950868.73 | 784777.03 | 1901080.25 | 82.5326 | 19.6473 | 19.6473 | 15-20 | 82.5326 | 19.6473 | 15-20 |  | 78918.95 | 2.6413 | 0-5 | Export to F09-MARNAYAKANAPALYA feeder
7 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F01-CIPSA | 1320105902010100 | INDUSTRIAL | 4.8 | 3.6 | 8.4 | 1 | 1 | 0 | 126.14 | 103.85 | 22.29 | 20000 | 445800 | 1 | 445800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 445800 |  | 0 | 472520 | 0 | 472520 | 472520 | -26720 | -5.9937 | <0 | -5.99 | 105.9937 | 105.9937 | 0 | 4359274 | 4359274 | 0 | 100 | -5.9937 | -5.9937 | <0 | 100 | -5.9937 | <0 |  | 472520 | -5.9937 | <0 |  | Dedicated Feeder (THT-177)
8 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F03-HARALURU | 1320105902010100 | AGRI | 5.3 | 4 | 9.3 | 90 | 93 | 379 | 564.96 | 559.63 | 5.33 | 40000 | 213200 | 1 | 213200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 213200 |  | 0 | 3029 | 197213.543 | 200242.543 | 192625.113 | 12957.457 | 6.0776 | 5-10 | 9.65 | 93.9224 | 93.9224 | 649755 | 1767537.56 | 1757615.81 | 659676.75 | 99.4387 | 6.6048 | 6.6048 | 5-10 | 99.4387 | 6.6048 | 5-10 |  | 200242.543 | 6.0776 | 5-10
9 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F04-INCAP | 1320105902010100 | MIXED LOAD | 0 | 0 | 0 | 38 | 1211 | 0 | 868.6 | 845.81 | 22.79 | 40000 | 911600 | 1 | 911600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 70000 |  |  |  | 841600 |  | 0 | 780894 | 0 | 780894 | 780894 | 60706 | 7.2132 | 5-10 | 7.21 | 92.7868 | 92.7868 | 7350670.19 | 7559719.79 | 7009454.99 | 7900934.99 | 92.7211 | 13.967 | 13.967 | 10-15 | 92.7211 | 13.967 | 10-15 |  | 780894 | 7.2132 | 5-10 | Export to F09-KESARAMODU-NJY feeder due to load changeover
10 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F05-INDUSTRIAL | 1320105902010100 | INDUSTRIAL | 1.2 | 0 | 1.2 | 38 | 204 | 0 | 4104.19 | 4020.19 | 84 | 20000 | 1680000 | 1 | 1680000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400000 |  |  | 1680000 |  | 400000 | 1188824.45 | 0 | 1588824.45 | 1588824.45 | 91175.55 | 5.4271 | 5-10 | 5.43 | 94.5729 | 94.5729 | 8449752.66 | 12542804.67 | 12336528.37 | 8656028.96 | 98.3554 | 6.9824 | 6.9824 | 5-10 | 98.3554 | 6.9824 | 5-10 |  | 1588824.45 | 5.4271 | 5-10
11 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F06-K-M-HALLI | 1320105902020300 | AGRI | 1.1 | 0 | 1.1 | 47 | 33 | 607 | 3235.1 | 3131.9 | 103.2 | 2000 | 206400 | 1 | 206400 | 0 | 0 | 0 | 0 | 250000 | 250000 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 456400 |  | 0 | 1925 | 410310.49 | 412235.49 | 412387.16 | 44164.51 | 9.6767 | 5-10 | 9.64 | 90.3233 | 90.3233 | 3074947.87 | 3743788.85 | 3736588.85 | 3082147.87 | 99.8077 | 9.8504 | 9.8504 | 5-10 | 99.8077 | 9.8504 | 5-10 |  | 412235.49 | 9.6767 | 5-10 | Import from F11-RAITHARAPALYA feeder due to load changeover
12 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F07-CARMOBILES | 1320105902020300 | INDUSTRIAL | 10 | 0 | 10 | 48 | 808 | 1 | 2114.65 | 2098.81 | 15.84 | 40000 | 633600 | 1 | 633600 | 0 | 0 | 0 | 0 | 1684900 | 1684900 | 0 | 0 | 0 | 0 | 9830 | 9830 | 1520121 |  |  | 2308670 |  | 1520121 | 563435.75 | 901.81 | 2084458.56 | 2094184.94 | 224211.44 | 9.7117 | 5-10 | 9.29 | 90.2883 | 90.2883 | 9142605.84 | 7460254.21 | 6980271.81 | 9622588.24 | 93.5661 | 15.5207 | 15.5207 | 15-20 | 93.5661 | 15.5207 | 15-20 |  | 2084458.56 | 9.7117 | 5-10 | Import from F16-TTP Newly charged feeder & Export to Dabaspet feeder due to sharing
13 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F08-HIREHALLI | 1320105902020300 | AGRI | 14 | 2 | 16 | 86 | 10 | 275 | 467.43 | 464.65 | 2.78 | 40000 | 111200 | 1 | 111200 | 0 | 0 | 0 | 0 | 49000 | 49000 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 160200 |  | 0 | 342 | 145180.714 | 145522.714 | 144740.664 | 14677.286 | 9.1619 | 5-10 | 9.65 | 90.8381 | 90.8381 | -515332.34 | 1312035.04 | 1309378.04 | -512675.34 | 99.7975 | 9.3458 | 9.3458 | 5-10 | 99.7975 | 9.3458 | 5-10 |  | 145522.714 | 9.1619 | 5-10 | Import from F10-SIDDAGANGA-MATA feeder due to load changeover
14 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F09-MARNAYAKANAPALYA | 1320105902020300 | DOMESTIC | 17 | 3 | 20 | 93 | 1299 | 90 | 1287.17 | 1274.29 | 12.88 | 40000 | 515200 | 1 | 515200 | 0 | 0 | 0 | 0 | 626000 | 626000 | 0 | 0 | 0 | 0 | 590000 | 590000 |  |  |  | 551200 |  | 0 | 449611 | 64839.952 | 514450.952 | 514503.852 | 36749.048 | 6.6671 | 5-10 | 6.66 | 93.3329 | 93.3329 | 12416621.9 | 5198220.17 | 4649598.11 | 12965243.96 | 89.446 | 16.5175 | 16.5175 | 15-20 | 89.446 | 16.5175 | 15-20 |  | 514450.952 | 6.6671 | 5-10 | Import from F14-SKS & Export to RAPDRP area of F09-MARNAYAKANAPALYA
| RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F09-MARNAYAKANAPALYA | 1320105902020300 | DOMESTIC |  |  |  |  | 2916 | 36 |  |  | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 590000 | 590000 |  |  |  |  | 0 | 0 |  |  |  | 590000 |  | 0 | 383343.01 | 148330 | 531673.01 |  | 58326.99 | 9.8859 | 5-10 | 6.66 | 90.1141 | 90.1141 | 7315389.36 | 5092977.93 | 4736244.93 | 7672002.36 | 92.9956 | 16.1979 | 16.1979 | 15-20 | 92.9956 | 16.1979 | 15-20 |  | 531673.01 | 9.8859 | 5-10 | Import from Non-RAPDRP area of F09-M.N.Palya
15 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F10-SIDDAGANGA-MATA | 1320105902020300 | DOMESTIC | 12 | 2 | 14 | 12 | 266 | 2 | 409 | 401.12 | 7.88 | 20000 | 157600 | 1 | 157600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49000 | 49000 |  |  |  | 108600 |  | 0 | 97287 | 1683.06 | 98970.06 | 98883.38 | 9629.94 | 8.8673 | 5-10 | 8.95 | 91.1327 | 91.1327 | 2729602.87 | 886727.76 | 806321.26 | 2810009.37 | 90.9322 | 17.1311 | 17.1311 | 15-20 | 90.9322 | 17.1311 | 15-20 |  | 98970.06 | 8.8673 | 5-10 | Export to F08-HIREHALLI feeder due to load changeover
16 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F11-RAITHARAPALYA | 1320105902020300 | NJY | 22 | 13 | 35 | 61 | 1164 | 3 | 1406.2 | 1371.8 | 34.4 | 20000 | 688000 | 1 | 688000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 250000 |  |  |  | 438000 |  | 0 | 396019.6 | 2149.9 | 398169.5 | 398414.17 | 39830.5 | 9.0937 | 5-10 | 9.04 | 90.9063 | 90.9063 | 12628271.91 | 4477995.83 | 4800729.64 | 12305538.1 | 107.2071 | 2.542 | 2.542 | 0-5 | 100 | 9.0937 | 5-10 |  | 398169.5 | 9.0937 | 5-10 | Export to F06-K-M-HALLI feeder due to load changeover
17 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F12-NANDIHALLI-NJY | 1320105902010100 | NJY | 18 | 7 | 25 | 41 | 682 | 0 | 3435.33 | 3353.9 | 81.43 | 20000 | 1628600 | 1 | 1628600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486190 | 486190 | 521678 |  |  | 1142410 |  | 521678 | 529671.75 | 0 | 1051349.75 | 1051349.75 | 91060.25 | 7.9709 | 5-10 | 7.97 | 92.0291 | 92.0291 | 180798.96 | 5632809.44 | 5530990.7 | 282617.7 | 98.1924 | 9.6344 | 9.6344 | 5-10 | 98.1924 | 9.6344 | 5-10 |  | 1051349.75 | 7.9709 | 5-10 | Export to Dabaspet Subdivision due to Sharing
18 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F14-RANE WALES | 1320105902010100 | INDUSTRIAL | 12 | 6 | 18 | 1 | 1 | 0 | 1331.95 | 1305.21 | 26.74 | 20000 | 534800 | 1 | 534800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520000 |  |  | 534800 |  | 520000 | 17340 | 0 | 537340 | 537340 | -2540 | -0.47494 | <0 | -0.47 | 100.4749 | 100.4749 | 0 | 889449 | 889449 | 0 | 100 | -0.47494 | -0.47494 | <0 | 100 | -0.47494 | <0 |  | 537340 | -0.47494 | <0 |  | Dedicated Feeder (THT-16)
19 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F15-KOLIHALLI | 1320105902020300 | AGRI |  |  |  | 5 | 0 | 240 | 645.76 | 636.48 | 9.28 | 20000 | 185600 | 1 | 185600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 185600 |  | 0 | 0 | 166685.577 | 166685.577 | 167690.257 | 18914.423 | 10.191 | 10-15 | 9.65 | 89.809 | 89.809 | 786502.21 | 1517595.96 | 1517597.91 | 786500.26 | 100.0001 | 10.1908 | 10.1908 | 10-15 | 100 | 10.191 | 10-15 |  | 166685.577 | 10.191 | 10-15
20 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNENAHALLI_66 | F03-KARENAHALLI IP | 1320104906010100 | AGRI | 16.6 | 12.6 | 29.2 | 28 | 74 | 487 | 10899.5 | 10736.6 | 162.9 | 2000 | 325800 | 1 | 325800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 325800 |  | 0 | 1029 | 294954.68 | 295983.68 | 294358.35 | 29816.32 | 9.1517 | 5-10 | 9.65 | 90.8483 | 90.8483 | 2952101.29 | 2675189.28 | 2671847.28 | 2955443.29 | 99.8751 | 9.2652 | 9.2652 | 5-10 | 99.8751 | 9.2652 | 5-10 |  | 295983.68 | 9.1517 | 5-10
21 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNENAHALLI_66 | F04-HONASIGERE IP | 1320104906010100 | AGRI | 20.6 | 15.3 | 35.9 | 32 | 0 | 296 | 8471.5 | 8307.2 | 164.3 | 2000 | 328600 | 1 | 328600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 328600 |  | 0 | 0 | 294877.89 | 294877.89 | 296888.98 | 33722.11 | 10.2624 | 10-15 | 9.65 | 89.7376 | 89.7376 | 2280735.07 | 2686845.41 | 2686845.41 | 2280735.07 | 100 | 10.2624 | 10.2624 | 10-15 | 100 | 10.2624 | 10-15 |  | 294877.89 | 10.2624 | 10-15
22 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F01-THAVAREKERE | 1320105903010100 | AGRI | 18 | 4 | 22 | 281 | 8 | 629 | 1252.123 | 1234.534 | 17.589 | 20000 | 351780 | 1 | 351780 | 0 | 0 | 0 | 0 | 239800 | 239800 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 591580 |  | 0 | 1027 | 527562.446 | 528589.446 | 534492.716 | 62990.554 | 10.6479 | 10-15 | 9.65 | 89.3521 | 89.3521 | 1498409.92 | 4839002.84 | 4833835.84 | 1503576.92 | 99.8932 | 10.7433 | 10.7433 | 10-15 | 99.8932 | 10.7433 | 10-15 |  | 528589.446 | 10.6479 | 10-15 | Import from F09-CNNL feeder due to load changeover
23 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F02-MULUKUNTE | 1320105903010100 | AGRI | 13 | 2 | 15 | 263 | 2 | 388 | 616.494 | 608.738 | 7.756 | 20000 | 155120 | 1 | 155120 | 0 | 0 | 0 | 0 | 57000 | 57000 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 212120 |  | 0 | 171 | 193154.64 | 193325.64 | 191650.2 | 18794.36 | 8.8602 | 5-10 | 9.65 | 91.1398 | 91.1398 | 2495695.24 | 1736226.76 | 1736228.76 | 2495693.24 | 100.0001 | 8.8601 | 8.8601 | 5-10 | 100 | 8.8602 | 5-10 |  | 193325.64 | 8.8602 | 5-10 | Import from F11-ARENAHALLI feeder due to load changeover
24 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F03-HONNUDIKE | 1320105903010100 | AGRI | 12 | 3 | 15 | 194 | 2 | 392 | 866.41 | 852.948 | 13.462 | 20000 | 269240 | 1 | 269240 | 0 | 0 | 0 | 0 | 60000 | 60000 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 329240 |  | 0 | 8 | 294859.164 | 294867.164 | 297467.324 | 34372.836 | 10.4401 | 10-15 | 9.65 | 89.5599 | 89.5599 | 2664068.97 | 2692430.18 | 2692008.18 | 2664490.97 | 99.9843 | 10.4541 | 10.4541 | 10-15 | 99.9843 | 10.4541 | 10-15 |  | 294867.164 | 10.4401 | 10-15 | Import from F08-HONNUDIKE-NJY feeder due to load changeover
25 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F04-SASALU | 1320105903010100 | AGRI | 18 | 5 | 23 | 331 | 3 | 282 | 750.608 | 740.987 | 9.621 | 20000 | 192420 | 1 | 192420 | 0 | 0 | 0 | 0 | 86000 | 86000 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 278420 |  | 0 | 106 | 244572.269 | 244678.269 | 251552.369 | 33741.731 | 12.119 | 10-15 | 9.65 | 87.881 | 87.881 | 1515345.46 | 2276874.1 | 2276016.1 | 1516203.46 | 99.9623 | 12.1521 | 12.1521 | 10-15 | 99.9623 | 12.1521 | 10-15 |  | 244678.269 | 12.119 | 10-15 | Import from F12-MAASKAL feeder due to load changeover
26 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F05-HOLAKALLU | 1320105903010100 | AGRI | 15 | 3 | 18 | 269 | 1 | 489 | 32.705 | 21.114 | 11.591 | 20000 | 231820 | 1 | 231820 | 0 | 0 | 0 | 0 | 64000 | 64000 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 295820 |  | 0 | 4 | 272899.744 | 272903.744 | 267272.104 | 22916.256 | 7.7467 | 5-10 | 9.65 | 92.2533 | 92.2533 | 842982.06 | 2418949.05 | 2418949.05 | 842982.06 | 100 | 7.7467 | 7.7467 | 5-10 | 100 | 7.7467 | 5-10 |  | 272903.744 | 7.7467 | 5-10 | Import from F10-HOLAKALLU-NJY feeder due to load changeover
27 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F06-CHOLAMBALLI | 1320105903020300 | AGRI | 14 | 2 | 16 | 331 | 9 | 410 | 888.385 | 875.404 | 12.981 | 20000 | 259620 | 1 | 259620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 259620 |  | 0 | 316 | 239289.668 | 239605.668 | 234567.408 | 20014.332 | 7.7091 | 5-10 | 9.65 | 92.2909 | 92.2909 | 3798630.27 | 2123699.73 | 2123885.84 | 3798444.16 | 100.0088 | 7.701 | 7.701 | 5-10 | 100 | 7.7091 | 5-10 |  | 239605.668 | 7.7091 | 5-10
28 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F07-VIRUPASANDRA | 1320105903020300 | AGRI | 18 | 6 | 24 | 85 | 1 | 233 | 827.294 | 816.514 | 10.78 | 20000 | 215600 | 1 | 215600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 45000 |  |  |  | 170600 |  | 0 | 15 | 155200.018 | 155215.018 | 194795.096 | 15384.982 | 9.0182 | 5-10 | 9.65 | 90.9818 | 90.9818 | 2510155.34 | 1398798.77 | 1398515.77 | 2510438.34 | 99.9798 | 9.0366 | 9.0366 | 5-10 | 99.9798 | 9.0366 | 5-10 |  | 155215.018 | 9.0182 | 5-10 | Export to Tumkur RSD-2 Subdivision due to sharing
29 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F08-HONNUDIKE-NJY | 1320105903020300 | NJY | 18 | 6 | 24 | 103 | 4990 | 0 | 1034.137 | 1012.62 | 21.517 | 20000 | 430340 | 1 | 430340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 60000 |  |  |  | 370340 |  | 0 | 334109.2 | 0 | 334109.2 | 334109.2 | 36230.8 | 9.7831 | 5-10 | 9.78 | 90.2169 | 90.2169 | 31548708.36 | 3579397.58 | 2772328.4 | 32355777.54 | 77.4524 | 30.1249 | 30.1249 | >30 | 77.4524 | 30.1249 | >30 |  | 334109.2 | 9.7831 | 5-10 | Export to F03-HONNUDIKE feeder due to load changeover
30 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F09-CNNL | 1320105903020300 | WATER WORKS | 26 | 7 | 33 | 1 | 1 | 0 | 566.953 | 554.849 | 12.104 | 20000 | 242080 | 1 | 242080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239800 | 239800 |  |  |  | 2280 |  | 0 | 2128 | 0 | 2128 | 2128 | 152 | 6.6667 | 5-10 | 6.67 | 93.3333 | 93.3333 | 27651349 | 773329 | 770000 | 27654678 | 99.5695 | 7.0684 | 7.0684 | 5-10 | 99.5695 | 7.0684 | 5-10 |  | 2128 | 6.6667 | 5-10 | Export to F01-THAVAREKERE feeder due to load changeover
31 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F10-HOLAKALLU-NJY | 1320105903020300 | NJY | 38 | 11.6 | 49.6 | 39 | 1417 | 0 | 594.72 | 583.593 | 11.127 | 20000 | 222540 | 1 | 222540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64000 | 64000 |  |  |  | 158540 |  | 0 | 141624 | 0 | 141624 | 143221 | 16916 | 10.6699 | 10-15 | 9.66 | 89.3301 | 89.3301 | 14568123.79 | 1410091.26 | 904662.06 | 15073552.99 | 64.1563 | 42.6891 | 42.6891 | >30 | 64.1563 | 42.6891 | >30 |  | 141624 | 10.6699 | 10-15 | Export to F05-HOLAKALLU feeder due to load changeover
32 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F11-ARENAHALLI | 1320105903020300 | NJY | 25 | 8.3 | 33.3 | 49 | 893 | 0 | 427 | 417.786 | 9.214 | 20000 | 184280 | 1 | 184280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57000 | 57000 |  |  |  | 127280 |  | 0 | 115079 | 0 | 115079 | 115079 | 12201 | 9.586 | 5-10 | 9.59 | 90.414 | 90.414 | 12255429.97 | 1226033.04 | 826229.91 | 12655233.1 | 67.3905 | 39.0695 | 39.0695 | >30 | 67.3905 | 39.0695 | >30 |  | 115079 | 9.586 | 5-10 | Export to F02-MULUKUNTE feeder due to load changeover
33 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F12-MAASKAL | 1320105903020300 | NJY | 38 | 15.3 | 53.3 | 52 | 1633 | 2 | 85.094 | 58.12 | 26.974 | 10000 | 269740 | 1 | 269740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86000 | 86000 |  |  |  | 183740 |  | 0 | 164868.2 | 1298.03 | 166166.23 | 166464.58 | 17573.77 | 9.5645 | 5-10 | 9.4 | 90.4355 | 90.4355 | 8234305.44 | 1756937.51 | 1635427.32 | 8355815.63 | 93.084 | 15.819 | 15.819 | 15-20 | 93.084 | 15.819 | 15-20 |  | 166166.23 | 9.5645 | 5-10 | Export to F04-SASALU feeder due to load changeover
34 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F13-VAHINI PIPES | 1320105903010300 | INDUSTRIAL | 28 | 7 | 35 | 1 | 2 | 0 | 60043.3 | 59441.9 | 601.4 | 2000 | 1202800 | 1 | 1202800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 1202800 |  | 0 | 1218500 | 0 | 1218500 | 1218500 | -15700 | -1.3053 | <0 | -1.31 | 101.3053 | 101.3053 | 4730.4 | 9295335.6 | 9293622 | 6444 | 99.9816 | -1.2866 | -1.2866 | <0 | 99.9816 | -1.2866 | <0 |  | 1218500 | -1.3053 | <0 |  | Dedicated Feeder (KSHT-20)
35 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F14-JOLUMARANAHALLI | 1320105903020300 | AGRI | 32 | 12 | 44 | 63 | 2 | 282 | 6811.1 | 6741.1 | 70 | 2000 | 140000 | 1 | 140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 140000 |  | 0 | 30 | 129045.3 | 129075.3 | 126489.52 | 10924.7 | 7.8034 | 5-10 | 9.65 | 92.1966 | 92.1966 | 4082464.87 | 1145116.24 | 1145115.24 | 4082465.87 | 99.9999 | 7.8034 | 7.8034 | 5-10 | 99.9999 | 7.8034 | 5-10 |  | 129075.3 | 7.8034 | 5-10
36 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F17-VAHINI PIPES UNIT-2 | 1320105903020310 | INDUSTRIAL |  |  |  |  | 1 | 0 | 1103.51 | 864.54 | 238.97 | 2000 | 477940 | 1 | 477940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 477940 |  | 0 | 475800 | 0 | 475800 | 475800 | 2140 | 0.44775 | 0-5 | 0.45 | 99.5522 | 99.5522 | 0 | 4393973 | 4393973 | 0 | 100 | 0.44775 | 0.44775 | 0-5 | 100 | 0.44775 | 0-5 |  | 475800 | 0.44775 | 0-5 |  | Dedicated Feeder (KSHT-55)
37 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F01-SEETHAKALLU | 1320105904010100 | AGRI | 19 | 7.3 | 26.3 | 140 | 15 | 385 | 1035.843 | 1013.756 | 22.087 | 20000 | 441740 | 1 | 441740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 441740 |  | 0 | 647 | 389689.871 | 390336.871 | 399113.251 | 51403.129 | 11.6365 | 10-15 | 9.65 | 88.3635 | 88.3635 | 8839014.17 | 3617974.84 | 3611724.13 | 8845264.88 | 99.8272 | 11.7892 | 11.7892 | 10-15 | 99.8272 | 11.7892 | 10-15 |  | 390336.871 | 11.6365 | 10-15
38 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F02-MYDALA | 1320105904010100 | NJY | 22 | 11.3 | 33.3 | 58 | 2319 | 1 | 1372.805 | 1345.942 | 26.863 | 10000 | 268630 | 1 | 268630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68000 | 68000 |  |  |  | 200630 |  | 0 | 180752.9 | 499.84 | 181252.74 | 181551.09 | 19377.26 | 9.6582 | 5-10 | 9.51 | 90.3418 | 90.3418 | 17701600.6 | 2133552.32 | 1449368.7 | 18385784.22 | 67.9322 | 38.6288 | 38.6288 | >30 | 67.9322 | 38.6288 | >30 |  | 181252.74 | 9.6582 | 5-10 | Export to F06-KURUVELU feeder due to load changeover
39 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F03-D.DURGA | 1320105904010100 | AGRI | 28 | 7 | 35 | 317 | 1 | 462 | 853.442 | 836.106 | 17.336 | 20000 | 346720 | 1 | 346720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 346720 |  | 0 | 12 | 313181.032 | 313193.032 | 313261.642 | 33526.968 | 9.6698 | 5-10 | 9.65 | 90.3302 | 90.3302 | 8364196.37 | 2835144.82 | 2835137.82 | 8364203.37 | 99.9998 | 9.67 | 9.67 | 5-10 | 99.9998 | 9.67 | 5-10 |  | 313193.032 | 9.6698 | 5-10
40 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F04-URDIGERE-RURAL | 1320105904010100 | AGRI | 18 | 7.3 | 25.3 | 376 | 17 | 479 | 894.543 | 871.495 | 23.048 | 20000 | 460960 | 1 | 460960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 460960 |  | 0 | 776 | 410160.25 | 410936.25 | 416478.34 | 50023.75 | 10.8521 | 10-15 | 9.65 | 89.1479 | 89.1479 | 10736784.67 | 3771819.8 | 3772653.7 | 10735950.77 | 100.0221 | 10.8324 | 10.8324 | 10-15 | 100 | 10.8521 | 10-15 |  | 410936.25 | 10.8521 | 10-15
41 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F05-KALENAHALLI | 1320105904020300 | NJY | 25 | 14 | 39 | 67 | 2414 | 2 | 702.457 | 687.951 | 14.506 | 20000 | 290120 | 1 | 290120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16000 | 16000 |  |  |  | 274120 |  | 0 | 249702 | 2083.08 | 251785.08 | 251298.38 | 22334.92 | 8.1479 | 5-10 | 8.33 | 91.8521 | 91.8521 | 15318211.6 | 2875266.65 | 2619389.86 | 15574088.39 | 91.1008 | 16.322 | 16.322 | 15-20 | 91.1008 | 16.322 | 15-20 |  | 251785.08 | 8.1479 | 5-10 | Export to F07-SATHAGHATTA feeder due to load changeover
42 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F06-KURUVELU | 1320105904020300 | AGRI | 16 | 6 | 22 | 120 | 7 | 509 | 780.75 | 768.792 | 11.958 | 20000 | 239160 | 1 | 239160 | 0 | 0 | 0 | 0 | 68000 | 68000 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 307160 |  | 0 | 302 | 281830.794 | 282132.794 | 277518.964 | 25027.206 | 8.1479 | 5-10 | 9.65 | 91.8521 | 91.8521 | 9095632.3 | 2512101.92 | 2511355.92 | 9096378.3 | 99.9703 | 8.1752 | 8.1752 | 5-10 | 99.9703 | 8.1752 | 5-10 |  | 282132.794 | 8.1479 | 5-10 | Import from F02-MYDALA feeder due to load changeover
43 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F07-SATHAGHATTA | 1320105904020300 | NJY | 12 | 5.3 | 17.3 | 109 | 4495 | 0 | 1687.072 | 1653.083 | 33.989 | 10000 | 339890 | 1 | 339890 | 0 | 0 | 0 | 0 | 16000 | 16000 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 355890 |  | 0 | 324336.1 | 0 | 324336.1 | 324336.1 | 31553.9 | 8.8662 | 5-10 | 8.87 | 91.1338 | 91.1338 | 28694304.39 | 3650409.85 | 2981545.27 | 29363168.97 | 81.677 | 25.5646 | 25.5646 | 20-30 | 81.677 | 25.5646 | 20-30 |  | 324336.1 | 8.8662 | 5-10 | Import from F05-KALENAHALLI feeder due to load changeover
44 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F08-HALUGONDANAHALLI | 1320105904010100 | AGRI | 18 | 5.6 | 23.6 | 38 | 6 | 444 | 948.558 | 929.731 | 18.827 | 20000 | 376540 | 1 | 376540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 376540 |  | 0 | 877 | 339746.176 | 340623.176 | 340205.036 | 35916.824 | 9.5386 | 5-10 | 9.65 | 90.4614 | 90.4614 | 8594858.7 | 3078254.55 | 3076001.92 | 8597111.33 | 99.9268 | 9.6048 | 9.6048 | 5-10 | 99.9268 | 9.6048 | 5-10 |  | 340623.176 | 9.5386 | 5-10
45 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F02-PALASANDRA | 1320105901010102 | AGRI |  |  |  | 1 | 0 | 1 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 265 | 265 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 265 |  | 0 | 0 | 241.78 | 241.78 |  | 23.22 | 8.7623 | 5-10 |  | 91.2377 | 91.2377 | -363.44 | 2188.11 | 2188.11 | -363.44 | 100 | 8.7623 | 8.7623 | 5-10 | 100 | 8.7623 | 5-10 |  | 241.78 | 8.7623 | 5-10 | Import from Tumkur CSD-2 Sub division
46 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F05-NJY-KITTAGANAHALLY | 1320105901010105 | NJY |  |  |  | 3 | 85 | 2 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 15800 | 15800 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 15800 |  | 0 | 12675 | 1596.38 | 14271.38 |  | 1528.62 | 9.6748 | 5-10 |  | 90.3252 | 90.3252 | 326992.03 | 133708.07 | 117574.07 | 343126.03 | 87.9334 | 20.574 | 20.574 | 20-30 | 87.9334 | 20.574 | 20-30 |  | 14271.38 | 9.6748 | 5-10 | Import from Tumkur CSD-2 Sub division
47 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F06-SANKAPURA | 1320105901010107 | AGRI |  |  |  | 6 | 85 | 61 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 60000 | 60000 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 60000 |  | 0 | 3638 | 51065.52 | 54703.52 |  | 5296.48 | 8.8275 | 5-10 |  | 91.1725 | 91.1725 | 570450.56 | 504749.96 | 496663.96 | 578536.56 | 98.398 | 10.288 | 10.288 | 10-15 | 98.398 | 10.288 | 10-15 |  | 54703.52 | 8.8275 | 5-10 | Import from Tumkur CSD-2 Sub division
48 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HEBBUR_66 | F01-HONASIGERE | 1320104903010101 | AGRI |  |  |  | 1 | 1 | 2 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 2360 | 2360 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2360 |  | 0 | 115 | 2031.32 | 2146.32 |  | 213.68 | 9.0542 | 5-10 |  | 90.9458 | 90.9458 | -1086.88 | 15068.4 | 14648.4 | -666.88 | 97.2127 | 11.5892 | 11.5892 | 10-15 | 97.2127 | 11.5892 | 10-15 |  | 2146.32 | 9.0542 | 5-10 | Import from Tumkur RSD-2 Sub division
49 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HEBBUR_66 | F08-BEGUR | 1320104903020304 | AGRI |  |  |  | 6 | 81 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 2850 | 2850 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2850 |  | 0 | 2602 | 0 | 2602 |  | 248 | 8.7018 | 5-10 |  | 91.2982 | 91.2982 | 320501.01 | 33780.41 | 33754.41 | 320527.01 | 99.923 | 8.772 | 8.772 | 5-10 | 99.923 | 8.772 | 5-10 |  | 2602 | 8.7018 | 5-10 | Import from Tumkur RSD-2 Sub division
50 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HEBBUR_66 | F13-DASARAHALLI NJY | 1320104903020501 | NJY |  |  |  | 3 | 2 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 3550 | 3550 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 3550 |  | 0 | 3220 | 0 | 3220 |  | 330 | 9.2958 | 5-10 |  | 90.7042 | 90.7042 | -52 | 22507.9 | 22502.9 | -47 | 99.9778 | 9.3159 | 9.3159 | 5-10 | 99.9778 | 9.3159 | 5-10 |  | 3220 | 9.2958 | 5-10 | Import from Tumkur RSD-2 Sub division
51 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HEBBUR_66 | F15-NIDUVALALU -NJY | 1320104903020500 | NJY |  |  |  | 24 | 466 | 1 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 26000 | 26000 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 26000 |  | 0 | 23189 | 604.91 | 23793.91 |  | 2206.09 | 8.485 | 5-10 |  | 91.515 | 91.515 | 2262063.65 | 283594.59 | 198776.15 | 2346882.09 | 70.0917 | 35.8556 | 35.8556 | >30 | 70.0917 | 35.8556 | >30 |  | 23793.91 | 8.485 | 5-10 | Import from Tumkur RSD-2 Sub division
52 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNENAHALLI_66 | F02-HONNENAHALLI IP | 1320104906010100 | AGRI |  |  |  | 15 | 3 | 203 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 127000 | 127000 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 127000 |  | 0 | 175 | 115302.943 | 115477.943 |  | 11522.057 | 9.0725 | 5-10 |  | 90.9275 | 90.9275 | 2892244.66 | 1037834.61 | 1037835.61 | 2892243.66 | 100.0001 | 9.0724 | 9.0724 | 5-10 | 100 | 9.0725 | 5-10 |  | 115477.943 | 9.0725 | 5-10 | Import from Tumkur RSD-2 Sub division
Sub division TOTAL | [7 empty] | 270.7 | 113.91 | 384.61 | 4332 | 46496 | 8710 |  |  |  |  | 19814760 |  | 19814760 |  |  |  |  | 4864525 | 4864525 |  |  |  |  | 3482820 | 3482820 | 2961799 | 0 | 2520 | 21198985 | 0 | 2961799 | 10553229.75 | 6086873.709 | 19601902.459 |  | 1597082.541 | 7.5338 | 5-10 |  | 92.4662 | 92.4662 | 322892663.37 | 163807255.04 | 158878625.94 | 327817485.47 | 96.9912 | 10.3159 | 10.3159 | 10-15 | 96.9912 | 10.3159 | 10-15 | 0 | 19601902.459 | 7.5338 | 5-10
Station Auxillary (Input & Sales) | [19 empty] | 6174.5 | [15 empty] | 6174.5
EHT Consumption
Above 11KV Wheeled Energy/ Open Access
IPP Consumption
Sub Division Grand Total | [7 empty] | 270.7 | 113.91 | 384.61 | 4332 | 46496 | 8710 |  |  |  |  | 19814760 |  | 19820934.5 |  |  |  |  | 4864525 | 4864525 |  |  |  |  | 3482820 | 3482820 | 2961799 | 0 | 2520 | 21205159.5 | 0 | 2961799 | 10553229.75 | 6086873.709 | 19601902.459 |  | 1597082.541 | 7.5316 | 5-10 |  | 92.4393 | 92.4393 | 322892663.37 | 163807255.04 | 158878625.94 | 327817485.47 | 96.9912 | 10.342 | 10.342 | 10-15 | 96.9912 | 10.342 | 10-15 | 0 | 19601902.459 | 7.5607 | 5-10
[20 empty] | 24164438.5 | [15 empty] | 2249220 | 2026657 | 9.8951
8318.7

## EHT Installations
Details of EHT Installations for the month of July-25 INPUT and August-25 DCB
Sl No | Division | Sub Division | Name of the EHT Consumer | RR No | Tariff | Date of Service (dd.mm.yyyy) | Contract Demand in KVA | Voltage Class | Station Name | Meter Details |  |  |  |  | Input in Units for the current month | Total EHT Sales Consumption in Units for the current month | EHT | Wheeled | Open Access | Remarks
[10 empty] | Meter make | Sl No | Conventional Meter / DLMS Meter | AMR facility available (Y/N) | Meter Working Condition
1 | [16 empty] | 0
2 | [16 empty] | 0
[15 empty] | 0 | 0 | 0 | 0 | 0 | 0
0
0
0
[15 empty] | 0 | 0 | 0 | 0 | 0 | 0
0
0
0
[15 empty] | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 | 0 | 0 | 0

## Wheeled Energy
List of Wheeled Energy Consumers for the month of July-25 INPUT and August-25 DCB
Sl No | Division | Sub Division | Name of the Wheeled Consumer | RR No | Tariff | Date of Service (dd.mm.yyyy) | Contract Demand in KVA | Voltage Class in KV | Station Name | Feeder No & Name | Type of Consumer (Captive & Non-Captive) | Wheeled units as per OM issued by PP section for the current month | Sales Consumption in Units for the current month | REMARKS
1 | TUMKUR | KYATSANDRA | CHAMUNDI DICAST PVT LTD | KHT5 | HT-2(a)(ii) | 1995-09-09 | 1200 | 11 KV | HIREHALLI | F05-INDUSTRIAL | NON-CAPTIVE | 400000 | 20780
2 | TUMKUR | KYATSANDRA | M S T.T.P. TECHNOLOGIES PVT LT | THT168 | HT-2(a)(ii) | 2008-11-04 | 1750 | 11 KV | HIREHALLI | F07-CARMOBILES | NON-CAPTIVE | 1044488 | 50137
3 | TUMKUR | KYATSANDRA | M/s T T P technology pvt ltd, Unit-3 | THT227 | HT-2(a)(ii) | 2011-11-02 | 1250 | 11 KV | HIREHALLI | F07-CARMOBILES | NON-CAPTIVE | 315633 | 285492
4 | TUMKUR | KYATSANDRA | M/S CHAMUNDI DIE CAST PVT LTD | KSHT33 | HT-2(a)(ii) |  | 600 | 11 KV | HIREHALLI | F07-CARMOBILES | NON-CAPTIVE | 160000 | 10670
5 | TUMKUR | KYATSANDRA | M/s Copprod Industries Pvt Ltd | THT173 | HT-2(a)(ii) | 2008-07-18 | 2000 | 11 KV | HIREHALLI | F12-NANDIHALLI-NJY | NON-CAPTIVE | 521678 | 273822
6 | TUMKUR | KYATSANDRA | RANE ENGINEVALVE LTD | THT16 | HT-2(a)(ii) | 1983-09-24 | 1600 | 11 KV | HIREHALLI | F14-RANE WALES | NON-CAPTIVE | 520000 | 17340
[12 empty] | 2961799 | 658241

## Open Access
List of Consumers availing power under Open Access for the month of July-25 INPUT and August-25 DCB
Sl No | Division | Sub Division | Name of the Wheeled Consumer | RR No | Tariff | Date of Service (dd.mm.yyyy) | Contract Demand in KVA | Voltage Class in KV | Station Name | Feeder No & Name | Type of Consumer (Captive & Non-Captive) | Open Access Input units for the current month | Sales Consumption in Units for the current month | Remarks

## IPP
List of IPP for the month of July-25 INPUT and August-25 DCB
Sl No | Division | Sub Division | Name of the IPP | Voltage Class in KV | Station Name | Feeder No & Name | Type of Consumer (Captive & Non-Captive) | Input in Mus for the current month | Remarks

## CF NEW
Correction Factor July-25 INPUT and August-25 DCB
Correction Factor
Sl. no | Particulars | Peak Load |  | Readings |  | Difference | MC | Net Energy in Units | Net Energy in MU |  | Difference | Correction Factor
|  | Amps | MW | Present | Previous |  |  |  | Bank | Feeder Total
BADDIHALLI_66
A | BANK-1 | 470 | 7.8 | 2030.921 | 1993.009 | 37.912 | 80000 | 3032960 | 3032960 | 3033420 | 460 |  | 6174.5
1 | F01-KITHAGANAHALLI | 130 | 2.1 | 822.450 | 810.293 | 12.157 | 20000 | 243140 |  |  |  | 0.99985
2 | F02-PALASANDRA | 170 | 2.8 | 878.208 | 867.411 | 10.797 | 20000 | 215940 |  |  |  | 0.99985
3 | F03-SAPTHAGIRI | 40 | 0.6 | 2240.594 | 2225.420 | 15.174 | 20000 | 303480 |  |  |  | 0.99985
4 | F04-MARUTHI NAGARA | 120 | 2 | 2385.326 | 2338.768 | 46.558 | 20000 | 931160 |  |  |  | 0.99985
5 | F05-NJY-KITTAGANAHALLY | 40 | 0.6 | 778.785 | 764.054 | 14.731 | 20000 | 294620 |  |  |  | 0.99985
6 | F06-SANKAPURA | 140 | 2.3 | 272.063 | 262.931 | 9.132 | 20000 | 182640 |  |  |  | 0.99985
7 | F13- Ragavendra nagara | 110 | 1.8 | 734.201 | 691.079 | 43.122 | 20000 | 862440
B | BANK-2 | 620 | 10.3 | 1590.29 | 1558.411 | 31.879 | 120000 | 3825480 | 3825480 | 3824764.1 | 715.9
8 | F07-GULARIVE | 150 | 2.5 | 820.406 | 811.238 | 9.168 | 20000 | 183360 |  |  |  | 1.0002
9 | F08-BADDIHALLI | 100 | 1.6 | 2271.322 | 2226.661 | 44.661 | 20000 | 893220 |  |  |  | 1.0002
10 | F09-KESARAMODU-NJY | 140 | 2.3 | 1976.441 | 1937.143 | 39.298 | 20000 | 785960 |  |  |  | 1.0002
11 | F10-CM-EXTENSION | 100 | 1.6 | 2129.246 | 2086.776 | 42.47 | 20000 | 849400 |  |  |  | 1.0002
12 | F11-KALAHALLI | 120 | 2 | 718.278 | 708.598 | 9.68 | 20000 | 193600 |  |  |  | 1.0002
13 | F12-KESARAMODU | 150 | 2.5 | 850.959 | 840.437 | 10.522 | 20000 | 210440 |  |  |  | 1.0002
14 | F14-SKS | 120 | 2 | 770.631 | 735.278 | 35.353 | 20000 | 707060 |  |  |  | 1.0002
| Sation Axu |  |  | 16949.67 | 16777.26 | 172.41 | 10 | 1724.1
Sl. no | Particulars | Peak Load |  | Readings |  | Difference | MC | Net Energy in Units | Net Energy in MU |  | Difference | Correction Factor
|  | Amps | MW | Present | Previous |  |  |  | Bank | Feeder Total
HIREHALLI_66
A | BANK-1 | 710 | 11.8333 | 2538.87 | 2488.468 | 50.402 | 120000 | 6048240 | 6048240 | 6025180 | 23060
1 | F01-CIPSA | 72 | 1.2 | 126.14 | 103.852 | 22.288 | 20000 | 445760 |  |  |  | 1.0038
2 | F02-HONNENAHALLI | 210 | 3.5 | 736.41 | 726.337 | 10.073 | 40000 | 402920 |  |  |  | 1.0038
3 | F03-HARALURU | 190 | 3.1667 | 564.96 | 559.632 | 5.328 | 40000 | 213120 |  |  |  | 1.0038
4 | F04-INCAP | 170 | 2.8333 | 868.6 | 845.808 | 22.792 | 40000 | 911680 |  |  |  | 1.0038
5 | F05-INDUSTRIAL | 202 | 3.3667 | 4104.19 | 4020.185 | 84.005 | 20000 | 1680100 |  |  |  | 1.0038
6 | F06-K-M-HALLI | 122 | 2.0333 | 3235.1 | 3131.9 | 103.2 | 2000 | 206400 |  |  |  | 1.0038
7 | F12-NANDIHALLI-NJY | 182 | 3.0333 | 3435.33 | 3353.904 | 81.426 | 20000 | 1628520 |  |  |  | 1.0038
| F-13 Auxilary |  |  | 84.4 | 82.6 | 1.8 | 1000 | 1800 |  |  |  | 1.0038
9 | F14-RANE WALES | 74 | 1.2333 | 1331.95 | 1305.206 | 26.744 | 20000 | 534880 |  |  |  | 1.0038
B | BANK-2 | 490 | 8.1667 | 3130.61 | 3097.456 | 33.154 | 120000 | 3978480 | 3978480 | 3976480 | 2000
10 | F07-CARMOBILES | 89 | 1.4833 | 2114.65 | 2098.807 | 15.843 | 40000 | 633720 |  |  |  | 1.0005
11 | F08-HIREHALLI | 60 | 1 | 467.43 | 464.648 | 2.782 | 40000 | 111280 |  |  |  | 1.0005
12 | F09-MARNAYAKANAPALYA | 80 | 1.3333 | 1287.17 | 1274.289 | 12.881 | 40000 | 515240 |  |  |  | 1.0005
13 | F10-SIDDAGANGA-MATA | 20 | 0.33333 | 409 | 401.119 | 7.881 | 20000 | 157620 |  |  |  | 1.0005
14 | F11-RAITHARAPALYA | 502 | 8.3667 | 1406.2 | 1371.799 | 34.401 | 20000 | 688020 |  |  |  | 1.0005
15 | F-15 Kolihalli | 116 | 1.9333 | 645.76 | 636.475 | 9.285 | 20000 | 185700 |  |  |  | 1.0005
16 | F-16 TTP | 180 | 3 | 11705.1 | 10020.2 | 1684.9 | 1000 | 1684900
Sl. no | Particulars | Peak Load |  | Readings |  | Difference | MC | Net Energy in Units | Net Energy in MU |  | Difference | Correction Factor
|  | Amps | MW | Present | Previous |  |  |  | Bank | Feeder Total
Honnudike_66
A | BANK-1 | 590 | 9.8333 | 1627.805 | 1599.836 | 27.969 | 60000 | 1678140 | 1678140 | 1678320 | -180
1 | F01-THAVAREKERE | 180 | 3 | 1252.123 | 1234.534 | 17.589 | 20000 | 351780 |  |  |  | 0.99989
2 | F02-MULUKUNTE | 140 | 2.3333 | 616.494 | 608.738 | 7.756 | 20000 | 155120 |  |  |  | 0.99989
3 | F03-HONNUDIKE | 164 | 2.7333 | 866.41 | 852.948 | 13.462 | 20000 | 269240 |  |  |  | 0.99989
4 | F04-SASALU | 194 | 3.2333 | 750.608 | 740.987 | 9.621 | 20000 | 192420 |  |  |  | 0.99989
5 | F05-HOLAKALLU | 180 | 3 | 32.705 | 21.114 | 11.591 | 20000 | 231820 |  |  |  | 0.99989
6 | F-17 VAHINI | 66 | 1.1 | 1103.51 | 864.54 | 238.97 | 2000 | 477940
B | BANK-2 | 696 | 11.6 | 2807.119 | 2778.031 | 29.088 | 120000 | 3490560 | 3490560 | 3487576 | 2984
7 | F06-CHOLAMBALLI | 142 | 2.3667 | 888.385 | 875.404 | 12.981 | 20000 | 259620 |  |  |  | 1.0009
8 | F07-VIRUPASANDRA | 150 | 2.5 | 827.294 | 816.514 | 10.78 | 20000 | 215600 |  |  |  | 1.0009
9 | F08-HONNUDIKE-NJY | 80 | 1.3333 | 1034.137 | 1012.62 | 21.517 | 20000 | 430340 |  |  |  | 1.0009
10 | F09-CNNL | 202 | 3.3667 | 566.953 | 554.849 | 12.104 | 20000 | 242080 |  |  |  | 1.0009
11 | F10-HOLAKALLU-NJY | 24 | 0.4 | 594.72 | 583.593 | 11.127 | 20000 | 222540 |  |  |  | 1.0009
12 | F11-ARENAHALLI | 32 | 0.53333 | 427 | 417.786 | 9.214 | 20000 | 184280 |  |  |  | 1.0009
13 | F12-MAASKAL | 44 | 0.73333 | 85.094 | 58.12 | 26.974 | 10000 | 269740 |  |  |  | 1.0009
14 | F13-VAHINI PIPES | 114 | 1.9 | 60043.3 | 59441.9 | 601.4 | 2000 | 1202800 |  |  |  | 1.0009
15 | F14-JOLUMARANAHALLI | 144 | 2.4 | 6811.1 | 6741.1 | 70 | 2000 | 140000 |  |  |  | 1.0009
16 | F15-NARUGANAHALLI IP | 96 | 1.6 | 3444.9 | 3339.8 | 105.1 | 2000 | 210200 |  |  |  | 1.0009
17 | F16-PANDITHANAHALLI IP | 66 | 1.1 | 2869.3 | 2814.7 | 54.6 | 2000 | 109200 |  |  |  | 1.0009
| Station Aux |  |  | 7137.1 | 7107.7 | 29.4 | 40 | 1176
Sl. no | Particulars | Peak Load |  | Readings |  | Difference | MC | Net Energy in Units | Net Energy in MU |  | Difference | Correction Factor
|  | Amps | MW | Present | Previous |  |  |  | Bank | Feeder Total
Urdigere_66
A | BANK-1 | 498 | 8.3 | 1122.793 | 1097.751 | 25.042 | 60000 | 1502520 | 1502520 | 1518050 | -15530
1 | F01-SEETHAKALLU | 200 | 3.3 | 1035.843 | 1013.756 | 22.087 | 20000 | 441740 |  |  |  | 0.98977
2 | F02-MYDALA | 45 | 0.7 | 1372.805 | 1345.942 | 26.863 | 10000 | 268630 |  |  |  | 0.98977
3 | F03-D.DURGA | 200 | 3.3 | 853.442 | 836.106 | 17.336 | 20000 | 346720 |  |  |  | 0.98977
4 | F04-URDIGERE-RURAL | 196 | 3.3 | 894.543 | 871.495 | 23.048 | 20000 | 460960 |  |  |  | 0.98977
B | BANK-2 | 270 | 4.5 | 1092.122 | 1071.414 | 20.708 | 60000 | 1242480 | 1242480 | 1247184.4 | -4704.4
5 | F05-KALENAHALLI | 72 | 1.2 | 702.457 | 687.951 | 14.506 | 20000 | 290120 |  |  |  | 0.99623
6 | F06-KURUVELU | 172 | 2.9 | 780.75 | 768.792 | 11.958 | 20000 | 239160 |  |  |  | 0.99623
7 | F07-SATHAGHATTA | 53 | 0.9 | 1687.072 | 1653.083 | 33.989 | 10000 | 339890 |  |  |  | 0.99623
8 | F08-HALUGONDANAHALLI | 180 | 3 | 948.558 | 929.731 | 18.827 | 20000 | 376540 |  |  |  | 0.99623
| Station Aux |  |  | 28765.94 | 28729.08 | 36.86 | 40 | 1474.4

## Comparision
Comparision Sheet (July-25 INPUT and August-25 DCB)
Sl no | Sub division | Input |  |  | Difference | No of Installations |  |  | Sales | Sales with EHT & Station Auxillary | Sales | Sales | Difference | Difference | Difference | Difference | Demand | Demand | Demand | Difference | Difference | collection | collection | collection | Difference | Difference
|  | As per Zone | As per feeder wise EA | As per feeder wise EA with EHT & Auxillary |  | As per feeder wise EA | As per RR sheet | As per DCB | As per feeder wise EA |  | As per RR sheet | As per DCB |  |  |  |  | As per feeder wise EA | As per RR sheet | As per 103 DCB |  |  | As per feeder wise EA | As per RR sheet | As per 103 DCB
1 | Kyathsandra |  | 21.199 | 21.2052 | -21.2052 | 55206 | 55206 | 55214 | 19.6019 | 19.6019 | 19.6019 | 19.6019 | [7 empty] | 0 | 0 |  |  |  | 0 | 0

## Feederwise Energy Audit (4) (hidden)
Feeder to Consumer Audit |  |  | July-25 INPUT and August-25 DCB
SL. No. | AREA- RAPDRP/Non_RAPDRP/sharing between RAPDRP & Non_RAPDRP | Sub Division | O&M Section | STATION | FEEDER NO.& NAME (as per MDM) | TOTAL ENERGY SALES in Units | Energy Loss in Units | %feeder Loss | T&D Loss Range | %Billing Efficiency | % BE with Assessed Sales | OB | Demand In Rs | Collection In Rs | CB | % Collection Efficiency | %AT&C loss | % AT & C LOSS with BE assessed | AT&C Loss Range 1 | Collection Efficiency restricted to 100% | % AT & C LOSS CE restricted to 100% | AT&C Loss Range-2 | Assessed Sales in Units | TOTAL Sales after assessment | Anaylized Feeder loss after assessing the energy | T&D Loss Range after assessment | Remarks (Assessed Energy/ Import/ Export/Others) | REMARKS & Reasons for -ve, above 10% for T & D LOSS | REMARKS & Reasons for-ve above 10% for AT&C LOSS | Action Plan for reducing the T&D LOSS | Methodology adopted to achieve T&Dloss below 3% | REMARKS & Reasons for-ve above 10% for AT&C LOSS
1 | 1a | 2 | 3 | 4 | 5 | 34=30+31+ 32+33 | 35=29-34 | 36=35/29*100 |  | 37=34/29*100 | 38=49/29*100 | 39 | 40 | 41 | 42 | 43=41/40*100 | 44=(1-(37*43)/ 10000)*100 | 45=((1-38*43/10000))*100 |  | 46 | 47=((1-38*46/10000))*100 |  | 48 | 49=34+48 | 50=(29-49)/29*100 |  | 47 | 48 |  |  |  | 49 | 415
1 | RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F08-BADDIHALLI | 821127.4 | #REF! | #REF! | #REF! | #REF! | #REF! | 2248116.08 | 7365459.07 | 2733750.85 | 3908887.08 | 37.1158 | #REF! | #REF! | #REF! | 37.1158 | #REF! | #REF! |  | 821127.4 | #REF! | #REF!
2 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F09-KESARAMODU-NJY | 770783 | #REF! | #REF! | #REF! | #REF! | #REF! | 9340332.22 | 7899596.57 | 5660743.62 | 11579185.17 | 71.6586 | #REF! | #REF! | #REF! | 71.6586 | #REF! | #REF! |  | 770783 | #REF! | #REF! | Import from due to load changeover
3 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F10-CM-EXTENSION | 92552.5 | #REF! | #REF! | #REF! | #REF! | #REF! | 187767.86 | 1157044.05 | 1096524.05 | 248287.86 | 94.7694 | #REF! | #REF! | #REF! | 94.7694 | #REF! | #REF! |  | 92552.5 | #REF! | #REF! | Export to RAPDRP area
| RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F10-CM-EXTENSION | 723655.9 | #REF! | #REF! | #REF! | #REF! | #REF! | 2008471.49 | 6426443.67 | 2137514 | 3138534.33 | 33.2612 | #REF! | #REF! | #REF! | 33.2612 | #REF! | #REF! | 125000 | 848655.9 | #REF! | #REF! | Import from NON-RAPDRP area
4 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F11-KALAHALLI | 319899.912 | #REF! | #REF! | #REF! | #REF! | #REF! | 4376178.73 | 1902581.39 | 1810837.39 | 4467922.73 | 95.1779 | #REF! | #REF! | #REF! | 95.1779 | #REF! | #REF! |  | 319899.912 | #REF! | #REF!
5 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F12-KESARAMODU | 425622.488 | #REF! | #REF! | #REF! | #REF! | #REF! | 608686.07 | 2479073.53 | 2477679.53 | 610080.07 | 99.9438 | #REF! | #REF! | #REF! | 99.9438 | #REF! | #REF! |  | 425622.488 | #REF! | #REF!
6 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F14-SKS | 58962 | #REF! | #REF! | #REF! | #REF! | #REF! | 1468807.43 | 727494.1 | 1337843.1 | 858458.43 | 183.8975 | #REF! | #REF! | #REF! | 100 | #REF! | #REF! |  | 58962 | #REF! | #REF! | Export to RAPDRP area of F09-Maranayakanapalya feeder, as F14-SKS feeder yet to be creataed in RAPDRP portal
7 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F01-CIPSA | 561510 | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 4968653 | 4968653 | 0 | 100 | #REF! | #REF! | #REF! | 100 | #REF! | #REF! |  | 561510 | #REF! | #REF! |  | Dedicated Feeder
8 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F03-HARALURU | 704343.445 | #REF! | #REF! | #REF! | #REF! | #REF! | 897935.81 | 4126619.39 | 4130661.36 | 893893.84 | 100.0979 | #REF! | #REF! | #REF! | 100 | #REF! | #REF! |  | 704343.445 | #REF! | #REF! | Import from F04-Incap feeder due to load changeover
9 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F04-INCAP | 713891 | #REF! | #REF! | #REF! | #REF! | #REF! | 6224686.57 | 7107121.98 | 6701859.84 | 6629948.71 | 94.2978 | #REF! | #REF! | #REF! | 94.2978 | #REF! | #REF! |  | 713891 | #REF! | #REF! | Export to F03- Haralur feeder due to load changeover
10 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F05-INDUSTRIAL | 1482746.05 | #REF! | #REF! | #REF! | #REF! | #REF! | 6225911.35 | 11201634.95 | 9883373.95 | 7544172.35 | 88.2315 | #REF! | #REF! | #REF! | 88.2315 | #REF! | #REF! |  | 1482746.05 | #REF! | #REF! | Export to F15-Kolihalli feeder due to load changeover
11 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F06-K-M-HALLI | 655038.746 | #REF! | #REF! | #REF! | #REF! | #REF! | 3249782.52 | 3829413.33 | 3824427.33 | 3254768.52 | 99.8698 | #REF! | #REF! | #REF! | 99.8698 | #REF! | #REF! |  | 655038.746 | #REF! | #REF! | Import from F11-Raitharapalya feeder due to load changeover
12 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F07-CARMOBILES | 1909251.25 | #REF! | #REF! | #REF! | #REF! | #REF! | 8529419.33 | 9463480.18 | 9446324.87 | 8546574.64 | 99.8187 | #REF! | #REF! | #REF! | 99.8187 | #REF! | #REF! |  | 1909251.25 | #REF! | #REF! | Import from new feeder F-16 TTP Technologies & Export to Dabbaspete Sub-Division
13 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F08-HIREHALLI | 416517.372 | #REF! | #REF! | #REF! | #REF! | #REF! | -404852.06 | 2426873.31 | 2425185.35 | -403164.1 | 99.9304 | #REF! | #REF! | #REF! | 99.9304 | #REF! | #REF! |  | 416517.372 | #REF! | #REF! | Import from F10-Siddaganga Mutt feeder due to load changeover
14 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F09-MARNAYAKANAPALYA | 581390.04 | #REF! | #REF! | #REF! | #REF! | #REF! | 12913682.5 | 5119585.39 | 4928878.64 | 13104389.25 | 96.275 | #REF! | #REF! | #REF! | 96.275 | #REF! | #REF! |  | 581390.04 | #REF! | #REF! | Import from F14-SKS feeder
| RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F09-MARNAYAKANAPALYA | 629412.07 | #REF! | #REF! | #REF! | #REF! | #REF! | 6263441.98 | 5100167.25 | 1953947 | 7518153.37 | 38.3114 | #REF! | #REF! | #REF! | 38.3114 | #REF! | #REF! | 15000 | 644412.07 | #REF! | #REF! | Import from F14-SKS feeder RAPDRP area
15 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F10-SIDDAGANGA-MATA | 169567.6 | #REF! | #REF! | #REF! | #REF! | #REF! | 2299503.68 | 1372252.39 | 625805.78 | 3045950.29 | 45.6043 | #REF! | #REF! | #REF! | 45.6043 | #REF! | #REF! |  | 169567.6 | #REF! | #REF! | Export to F08-Hirehalli feeder due to load changeover
16 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F11-RAITHARAPALYA | 474879.1 | #REF! | #REF! | #REF! | #REF! | #REF! | 9009338.45 | 4796410.41 | 2887741.37 | 10918007.49 | 60.2063 | #REF! | #REF! | #REF! | 60.2063 | #REF! | #REF! |  | 474879.1 | #REF! | #REF! | Export to F06-K-M Halli feeder due to load changeover
17 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F12-NANDIHALLI-NJY | 994266.25 | #REF! | #REF! | #REF! | #REF! | #REF! | 190689.38 | 3107823.04 | 3065785.02 | 232727.4 | 98.6473 | #REF! | #REF! | #REF! | 98.6473 | #REF! | #REF! |  | 994266.25 | #REF! | #REF! | SHARING WITH DABASPETE S/D
18 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F14-RANE WALES | 504300 | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 3721908 | 3721908 | 0 | 100 | #REF! | #REF! | #REF! | 100 | #REF! | #REF! |  | 504300 | #REF! | #REF! |  | Dedicated Feeder
19 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F15-KOLIHALLI | 444000 | #REF! | #REF! | #REF! | #REF! | #REF! | 932042.99 | 2584080 | 2584080 | 932042.99 | 100 | #REF! | #REF! | #REF! | 100 | #REF! | #REF! |  | 444000 | #REF! | #REF! | Import from F05-Industrial feeder due to load changeover
20 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNENAHALLI_66 | F03-KARENAHALLI IP | 709894.294 | #REF! | #REF! | #REF! | #REF! | #REF! | 3238177.29 | 4143624.74 | 4141227.81 | 3240574.22 | 99.9422 | #REF! | #REF! | #REF! | 99.9422 | #REF! | #REF! |  | 709894.294 | #REF! | #REF!
21 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNENAHALLI_66 | F04-HONASIGERE IP | 546981.975 | #REF! | #REF! | #REF! | #REF! | #REF! | 2500722.01 | 3183434.99 | 3183434.99 | 2500722.01 | 100 | #REF! | #REF! | #REF! | 100 | #REF! | #REF! |  | 546981.975 | #REF! | #REF!
22 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F01-THAVAREKERE | 1127301.571 | #REF! | #REF! | #REF! | #REF! | #REF! | 1854991.42 | 6565890.67 | 6556164.67 | 1864717.42 | 99.8519 | #REF! | #REF! | #REF! | 99.8519 | #REF! | #REF! |  | 1127301.571 | #REF! | #REF! | Import from F09-CNNL feeder due to load changeover
23 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F02-MULUKUNTE | 531216.572 | #REF! | #REF! | #REF! | #REF! | #REF! | 2683387 | 3094115.98 | 3093650.08 | 2683852.9 | 99.9849 | #REF! | #REF! | #REF! | 99.9849 | #REF! | #REF! |  | 531216.572 | #REF! | #REF! | Import from F12-Maaskal feeder due to load changeover
24 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F03-HONNUDIKE | 724326.369 | #REF! | #REF! | #REF! | #REF! | #REF! | 2901702 | 4215865.34 | 4215520.34 | 2902047 | 99.9918 | #REF! | #REF! | #REF! | 99.9918 | #REF! | #REF! |  | 724326.369 | #REF! | #REF! | Import from F08-Honnudike NJY feeder due to load changeover
25 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F04-SASALU | 476645.027 | #REF! | #REF! | #REF! | #REF! | #REF! | 1647058 | 2774517.21 | 2774913.21 | 1646662 | 100.0143 | #REF! | #REF! | #REF! | 100 | #REF! | #REF! |  | 476645.027 | #REF! | #REF!
26 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F05-HOLAKALLU | 915705 | #REF! | #REF! | #REF! | #REF! | #REF! | 981975.33 | 5329527.01 | 5329527.01 | 981975.33 | 100 | #REF! | #REF! | #REF! | 100 | #REF! | #REF! |  | 915705 | #REF! | #REF! | Import from F10-Holakallu NJY feeder due to load changeover
27 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F06-CHOLAMBALLI | 747293.688 | #REF! | #REF! | #REF! | #REF! | #REF! | 4041883.31 | 4350730.96 | 4351343.96 | 4041270.31 | 100.0141 | #REF! | #REF! | #REF! | 100 | #REF! | #REF! |  | 747293.688 | #REF! | #REF!
28 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F07-VIRUPASANDRA | 399683.356 | #REF! | #REF! | #REF! | #REF! | #REF! | 3320205.99 | 2326606.49 | 2325947.316 | 3320864.95 | 99.9717 | #REF! | #REF! | #REF! | 99.9717 | #REF! | #REF! |  | 399683.356 | #REF! | #REF! | Export to Tumkur RSD-2 Subdivision due to sharing
29 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F08-HONNUDIKE-NJY | 370988.8 | #REF! | #REF! | #REF! | #REF! | #REF! | 27463573.42 | 3653750.92 | 2363245.03 | 28754079.31 | 64.68 | #REF! | #REF! | #REF! | 64.68 | #REF! | #REF! |  | 370988.8 | #REF! | #REF! | Export to F03-Honnudike feeder due to load changeover
30 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F09-CNNL | 352 | #REF! | #REF! | #REF! | #REF! | #REF! | 27531362 | 753983 | 2800000 | 25485345 | 371.3612 | #REF! | #REF! | #REF! | 100 | #REF! | #REF! |  | 352 | #REF! | #REF! | Export to F01-Thavarekere feeder due to load changeover
31 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F10-HOLAKALLU-NJY | 138912 | #REF! | #REF! | #REF! | #REF! | #REF! | 12782292.38 | 1350854.72 | 1165905.96 | 12967241.14 | 86.3088 | #REF! | #REF! | #REF! | 86.3088 | #REF! | #REF! | 2000 | 140912 | #REF! | #REF! | Export to F05-Holakallu feeder due to load changeover
32 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F11-ARENAHALLI | 121090 | #REF! | #REF! | #REF! | #REF! | #REF! | 10793711.75 | 1258885.23 | 866941.23 | 11185655.75 | 68.8658 | #REF! | #REF! | #REF! | 68.8658 | #REF! | #REF! |  | 121090 | #REF! | #REF! | Import from F12-Maaskal feeder due to load changeover
33 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F12-MAASKAL | 156560.2 | #REF! | #REF! | #REF! | #REF! | #REF! | 7455886.03 | 1652754.19 | 912974.19 | 8195666.03 | 55.2396 | #REF! | #REF! | #REF! | 55.2396 | #REF! | #REF! |  | 156560.2 | #REF! | #REF! | Export to F02-Mulukunte & F11-Arenahalli feeder due to load changeover
34 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F13-VAHINI PIPES | 1504850 | #REF! | #REF! | #REF! | #REF! | #REF! | 3004 | 12111919 | 12111919 | 3004 | 100 | #REF! | #REF! | #REF! | 100 | #REF! | #REF! |  | 1504850 | #REF! | #REF! |  | Dedicated Feeder
35 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F14-JOLUMARANAHALLI | 387522 | #REF! | #REF! | #REF! | #REF! | #REF! | 4208439 | 2255802.22 | 2255515.22 | 4208726 | 99.9873 | #REF! | #REF! | #REF! | 99.9873 | #REF! | #REF! |  | 387522 | #REF! | #REF!
36 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F01-SEETHAKALLU | 684323.356 | #REF! | #REF! | #REF! | #REF! | #REF! | 9077766.09 | 3990078.35 | 3997457.64 | 9070386.8 | 100.1849 | #REF! | #REF! | #REF! | 100 | #REF! | #REF! |  | 684323.356 | #REF! | #REF!
37 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F02-MYDALA | 204699.21 | #REF! | #REF! | #REF! | #REF! | #REF! | 15718462.5 | 2051560.63 | 1813559.63 | 15956463.5 | 88.399 | #REF! | #REF! | #REF! | 88.399 | #REF! | #REF! |  | 204699.21 | #REF! | #REF! | Export to F08-Halugondanahalli feeder due to load changeover
38 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F03-D.DURGA | 636703.428 | #REF! | #REF! | #REF! | #REF! | #REF! | 8557862.26 | 3705784.59 | 3705775.59 | 8557871.26 | 99.9998 | #REF! | #REF! | #REF! | 99.9998 | #REF! | #REF! |  | 636703.428 | #REF! | #REF! | Import from F05-Kalenahalli feeder due to load changeover
39 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F04-URDIGERE-RURAL | 813394 | #REF! | #REF! | #REF! | #REF! | #REF! | 11030746.05 | 4738238.77 | 4738198.77 | 11030786.05 | 99.9992 | #REF! | #REF! | #REF! | 99.9992 | #REF! | #REF! |  | 813394 | #REF! | #REF! | Import from F07-Sathaghastta feeder due to load changeover
40 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F05-KALENAHALLI | 233329.8 | #REF! | #REF! | #REF! | #REF! | #REF! | 13802099.85 | 2576029.03 | 2501161.61 | 13876967.27 | 97.0937 | #REF! | #REF! | #REF! | 97.0937 | #REF! | #REF! |  | 233329.8 | #REF! | #REF! | Export to F03-D.Durga feeder due to load changeover
41 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F06-KURUVELU | 622349.644 | #REF! | #REF! | #REF! | #REF! | #REF! | 9284504.1 | 3623271.1 | 3622877.12 | 9284898.08 | 99.9891 | #REF! | #REF! | #REF! | 99.9891 | #REF! | #REF! |  | 622349.644 | #REF! | #REF!
42 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F07-SATHAGHATTA | 349308.5 | #REF! | #REF! | #REF! | #REF! | #REF! | 25706962.98 | 3632867.93 | 2632781.73 | 26707049.18 | 72.4712 | #REF! | #REF! | #REF! | 72.4712 | #REF! | #REF! |  | 349308.5 | #REF! | #REF! | Export to F03-D.Durga feeder due to load changeover
43 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F08-HALUGONDANAHALLI | 586583.16 | #REF! | #REF! | #REF! | #REF! | #REF! | 8749049.89 | 3416374.95 | 3409488.32 | 8755936.52 | 99.7984 | #REF! | #REF! | #REF! | 99.7984 | #REF! | #REF! |  | 586583.16 | #REF! | #REF! | Import from F02-Mydala feeder due to load changeover
46 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F05-NJY-KITTAGANAHALLY | 26717.9 | #REF! | #REF! | #REF! | #REF! | #REF! | 1653017.22 | 253773.63 | 208401.63 | 1698389.22 | 82.1211 | #REF! | #REF! | #REF! | 82.1211 | #REF! | #REF! |  | 26717.9 | #REF! | #REF! | Import from RSD-2 Sub division
47 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F06-SANKAPURA | 97003.062 | #REF! | #REF! | #REF! | #REF! | #REF! | 604072.02 | 581147.42 | 579507.42 | 605712.02 | 99.7178 | #REF! | #REF! | #REF! | 99.7178 | #REF! | #REF! |  | 97003.062 | #REF! | #REF! | Import from RSD-2 Sub division
48 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HEBBUR_66 | F08-BEGUR | 720512.45 | #REF! | #REF! | #REF! | #REF! | #REF! | 3013122.97 | 4222088.87 | 4197736.633 | 3037475.16 | 99.4232 | #REF! | #REF! | #REF! | 99.4232 | #REF! | #REF! |  | 720512.45 | #REF! | #REF! | Import from RSD-2 Sub division
49 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HEBBUR_66 | F13-DASARAHALLI NJY | 128165.84 | #REF! | #REF! | #REF! | #REF! | #REF! | 17957875.09 | 1166655.6 | 641408.98 | 18483121.71 | 54.9784 | #REF! | #REF! | #REF! | 54.9784 | #REF! | #REF! |  | 128165.84 | #REF! | #REF! | Import from RSD-2 Sub division
44 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HEBBUR_66 | F15-NIDUVALALU -NJY | 128043.45 | #REF! | #REF! | #REF! | #REF! | #REF! | 11667148.87 | 1260710.37 | 530952.71 | 12396906.53 | 42.1154 | #REF! | #REF! | #REF! | 42.1154 | #REF! | #REF! |  | 128043.45 | #REF! | #REF! | Import from RSD-2 Sub division
45 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNENAHALLI_66 | F02-HONNENAHALLI IP | 578294.46 | #REF! | #REF! | #REF! | #REF! | #REF! | 3420155.98 | 3367885.3 | 3366336.09 | 3421704.98 | 99.954 | #REF! | #REF! | #REF! | 99.954 | #REF! | #REF! |  | 578294.46 | #REF! | #REF! | Import from RSD-2 Sub division
Sub division TOTAL | [5 empty] | 28122467.235 | #REF! | #REF! | #REF! | #REF! | #REF! | 330221159.18 | 194492444.21 | 172797397.939 | 343894892.07 | 88.8453 | #REF! | #REF! | #REF! | 88.8453 | #REF! | #REF! | 140000 | 28264467.235 | #REF! | #REF!
Station Auxillary (Input & Sales)
EHT Consumption
Above 11KV Wheeled Energy/ Open Access
IPP Consumption
Sub Division Grand Total | [5 empty] | 28122467.235 | #REF! | #REF! | #REF! | #REF! | #REF! | 330221159.18 | 194492444.21 | 172797397.939 | 343894892.07 | 88.8453 | #REF! | #REF! | #REF! | 88.8453 | #REF! | #REF! | 140000 | 28264467.235 | #REF! | #REF!

## Feederwise Energy Audit (3) (hidden)
Feeder to Consumer Audit (SEP-24 INPUT and OCT-24 DCB)
SL. No. | AREA- RAPDRP/Non_RAPDRP/sharing between RAPDRP & Non_RAPDRP | Sub Division | O&M Section | STATION | FEEDER NO.& NAME (as per MDM) | FEEDER METER READING DETAILS | [5 empty] | TOTAL INPUT ENERGY (FEEDER CONSUMPTION + IMPORT-EXPORT+SRTPV) in Units |  | TOTAL ENERGY SALES in Units |  | OB | Demand In Rs | Collection In Rs | CB | Remarks (Assessed Energy/ Import/ Export/Others) | REMARKS & Reasons for -ve, above 10% for T & D LOSS | REMARKS & Reasons for-ve above 10% for AT&C LOSS | Action Plan for reducing the T&D LOSS | Methodology adopted to achieve T&Dloss below 3% | REMARKS & Reasons for-ve above 10% for AT&C LOSS
[6 empty] | FR | IR | TOTAL IMPORT IN UNITS |  | TOTAL EXPORT IN UNITS
1 | 1a | 2 | 3 | 4 | 5 | 11 | 12 | 21=(20*A)+B |  | 25=(24*C)+D |  | 29=17+21-25+28 |  | 34=30+31+ 32+33 |  | 39 | 40 | 41 | 42 | 47 | 48 |  |  |  | 49 | 344
1 | RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F08-BADDIHALLI | 1834.35 | 1794.56 | 0 | 0 | 0 | 0 | 795800 | 0.7958 | 750965.98 | 0.75097 | 5113887.79 | 6621070.79 | 4392576.04 | 4372545.23
2 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F09-KESARAMODU-NJY | 1606.61 | 1572.74 | 90000 | 0.09 | 0 | 0 | 767400 | 0.7674 | 702231 | 0.70223 | 20739484.97 | 7033740 | 19632509.65 | 8140715.32 | Import from HF-10 SS Mutt feeder due to load changeover
3 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F10-CM-EXTENSION | 1710.89 | 1676.83 | 0 | 0 | 596000 | 0.596 | 85200 | 0.0852 | 79208.5 | 0.079209 | 1851920 | 1075543.09 | 3046876.09 | -119413 | Export to RAPDRP area
4 | RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F10-CM-EXTENSION |  |  | 596000 | 0.596 | 0 | 0 | 596000 | 0.596 | 573534.9 | 0.57353 | 2353482.41 | 5236926.41 | 2400169.04 | 2344553.22 | Import from RAPDRP area
5 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F11-KALAHALLI | 618.52 | 611.87 | 0 | 0 | 0 | 0 | 133000 | 0.133 | 120573 | 0.12057 | 8913932.94 | 732280 | 5656063 | 3990149.94
6 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F12-KESARAMODU | 719.84 | 712.38 | 0 | 0 | 0 | 0 | 149200 | 0.1492 | 135008 | 0.13501 | 701520 | 731550.61 | 844102.61 | 588968
7 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F14-SKS | 423.5 | 393.34 | 0 | 0 | 542600 | 0.5426 | 60600 | 0.0606 | 56064.5 | 0.056065 | 5501328 | 771335.49 | 3570516.49 | 2702147 | Newly charged feeder, Installations yet to be tagged Energy is exported to F09-Maranayakanapalya feeder
8 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F01-CIPSA | 1080.02 | 1054.8 | 0 | 0 | 0 | 0 | 504400 | 0.5044 | 504640 | 0.50464 | -4435 | 4260891 | 4256456 | 0 | Dedicated Feeder
9 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F03-HARALURU | 469.14 | 465.46 | 25000 | 0.025 | 0 | 0 | 172200 | 0.1722 | 156041 | 0.15604 | 1012577 | 867795.93 | 976075.93 | 904297 | Import from HF-04 CARMOBILE Feeder due to load changeover
10 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F04-INCAP | 650.73 | 627.82 | 0 | 0 | 25000 | 0.025 | 891400 | 0.8914 | 809693 | 0.80969 | 18469079.99 | 7535744.51 | 20775990.51 | 5228833.99 | Export to HF-03 Haralur feeder due to load changeover
11 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F05-INDUSTRIAL | 3357.72 | 3287.48 | 0 | 0 | 0 | 0 | 1404800 | 1.4048 | 1328870.75 | 1.3289 | 15660188 | 9956418.94 | 19306487.94 | 6310119 | Import from HF-07 Carmobile feeder due to load changeover
12 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F06-K-M-HALLI | 1917.4 | 1838.9 | 120000 | 0.12 | 0 | 0 | 277000 | 0.277 | 250834 | 0.25083 | 3227233 | 1368844.04 | 1367782.04 | 3228295 | Import from HF-07 Carmobile feeder due to load changeover
13 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F07-CARMOBILES | 1925.18 | 1887.71 | 0 | 0 | 125000 | 0.125 | 1373800 | 1.3738 | 1242972.25 | 1.243 | 24098228.78 | 5169266.7 | 22140842.71 | 7126652.77 | Export to HF-06 K M Halli feeder due to load changeover & Sharing with Dabuspet Subdivision
14 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F08-HIREHALLI | 429.08 | 426.92 | 75000 | 0.075 | 0 | 0 | 161400 | 0.1614 | 145824 | 0.14582 | -405757 | 788903.43 | 789431.43 | -406285 | Import from HF-11 Raitharapalya feeder due to load changeover
15 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F09-MARNAYAKANAPALYA | 1169.08 | 1158.98 | 85000 | 0.085 | 0 | 0 | 489000 | 0.489 | 463485 | 0.46348 | 21522249.99 | 4404865.93 | 14766343.93 | 11160771.99 | Import from HF-10 S S MUTT feeder due to load changeover
16 | RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F09-MARNAYAKANAPALYA |  |  | 542600 | 0.5426 | 0 | 0 | 542600 | 0.5426 | 516796 | 0.5168 | 7366523.72 | 4108464.87 | 2942906 | 6875944.72 | Import from F14-SKS feeder RAPDRP area
17 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F10-SIDDAGANGA-MATA | 330.63 | 322.35 | 0 | 0 | 90000 | 0.09 | 75600 | 0.0756 | 69940 | 0.06994 | 5247921.94 | 648653.6 | 3985985.6 | 1910589.94 | Export to BF-09 Kesaramadu NJY feeder due to load changeover
18 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F11-RAITHARAPALYA | 1101.2 | 1072.07 | 0 | 0 | 75000 | 0.075 | 507600 | 0.5076 | 472949.5 | 0.47295 | 22106826.08 | 4687015.34 | 17998296.34 | 8795545.08 | Export to HF-08 Hirehalli feeder due to load changeover
19 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F12-NANDIHALLI-NJY | 2667.04 | 2601.67 | 0 | 0 | 298000 | 0.298 | 1009400 | 1.0094 | 914322 | 0.91432 | -583021 | 4390095.03 | 3533794.03 | 273280 | Sharing with Dabuspet Subdivision
20 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F14-RANE WALES | 1082.28 | 1058.34 | 0 | 0 | 0 | 0 | 478800 | 0.4788 | 480100 | 0.4801 | -1629 | 585620 | 583991 | 0 | Dedicated Feeder
21 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F15-KOLIHALLI | 513.82 | 506.81 | 0 | 0 | 0 | 0 | 140200 | 0.1402 | 126967 | 0.12697 | 932043 | 684352.13 | 684352.13 | 932043
22 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNENAHALLI_66 | F03-KARENAHALLI IP | 8203.2 | 8051.2 | 0 | 0 | 0 | 0 | 304000 | 0.304 | 275200 | 0.2752 | 3449333.01 | 1497283.31 | 1618773.31 | 3327843.01
23 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNENAHALLI_66 | F04-HONASIGERE IP | 6664.9 | 6616.1 | 0 | 0 | 0 | 0 | 97600 | 0.0976 | 88393 | 0.088393 | 2500722 | 476438.27 | 476438.27 | 2500722
24 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F01-THAVAREKERE | 991.71 | 979.95 | 0 | 0 | 0 | 0 | 235200 | 0.2352 | 213066 | 0.21307 | 1846287 | 1150614.66 | 1148132.66 | 1848769
25 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F02-MULUKUNTE | 500.07 | 496.19 | 0 | 0 | 0 | 0 | 77600 | 0.0776 | 70235 | 0.070235 | 2682864 | 381093.75 | 381095.75 | 2682862
26 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F03-HONNUDIKE | 662.16 | 655.1 | 22000 | 0.022 | 0 | 0 | 163200 | 0.1632 | 147584 | 0.14758 | 2901513 | 795776.35 | 795375.35 | 2901914 | Import from HNF-08 Honnudike NJY feeder due to load changeover
27 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F04-SASALU | 614.7 | 609.17 | 38000 | 0.038 | 0 | 0 | 148600 | 0.1486 | 134650 | 0.13465 | 1646296 | 726426.72 | 725845.72 | 1646877 | Import from HNF-09 CNNL feeder due to load changeover
28 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F05-HOLAKALLU | 1004.79 | 994.28 | 90000 | 0.09 | 0 | 0 | 300200 | 0.3002 | 271707 | 0.27171 | 981975 | 1464628.54 | 1464628.54 | 981975 | Import from HNF-10 HOLAKALLU NJY feeder due to load changeover
29 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F06-CHOLAMBALLI | 671.68 | 664.45 | 7000 | 0.007 | 0 | 0 | 151600 | 0.1516 | 137220 | 0.13722 | 4042723 | 741092.99 | 739707.99 | 4044108 | Import from HNF-11 Arehalli NJY feeder due to load changeover
30 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F07-VIRUPASANDRA | 692.23 | 687.35 | 0 | 0 | 20000 | 0.02 | 77600 | 0.0776 | 69886 | 0.069886 | 2637927 | 377185.23 | 377189.23 | 2637923 | Exported units belongs to RSD-2 Sub-Division
31 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F08-HONNUDIKE-NJY | 820.77 | 802.21 | 0 | 0 | 22000 | 0.022 | 349200 | 0.3492 | 320632 | 0.32063 | 76471955.36 | 3638986.73 | 56301863.71 | 23809078.38 | Export to HNF-03 Honnudike feeder due to load changeover
32 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F09-CNNL | 436.89 | 433.45 | 0 | 0 | 38000 | 0.038 | 30800 | 0.0308 | 28280 | 0.02828 | 21287153 | 881335 | 728000 | 21440488 | Export to HNF-04 Sasalu feeder due to load changeover
33 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F10-HOLAKALLU-NJY | 476.3 | 464.59 | 0 | 0 | 90000 | 0.09 | 144200 | 0.1442 | 130833 | 0.13083 | 27203252 | 1332359.31 | 17636532.77 | 10899078.54 | Export to HNF-05 HOLAKALLU feeder due to load changeover
34 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F11-ARENAHALLI | 361.12 | 355.02 | 0 | 0 | 7000 | 0.007 | 115000 | 0.115 | 105156 | 0.10516 | 21942300.16 | 1156155.86 | 13113741.86 | 9984714.16 | Export to HNF-06 Cholamballi feeder due to load changeover
35 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F12-MAASKAL | 793.02 | 771.01 | 0 | 0 | 90000 | 0.09 | 130100 | 0.1301 | 118415 | 0.11842 | 17955968.63 | 1415588.64 | 12511069.62 | 6860487.65 | Export to HNF-14 Jolumaranahalli feeder due to load changeover
36 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F13-VAHINI PIPES | 54662.8 | 54100.5 | 0 | 0 | 0 | 0 | 1124600 | 1.1246 | 1154100 | 1.1541 | 0 | 8675296 | 8675290 | 6 | Dedicated Feeder
37 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F14-JOLUMARANAHALLI | 5614.5 | 5553.2 | 90000 | 0.09 | 0 | 0 | 212600 | 0.2126 | 192348 | 0.19235 | 4208314 | 1037167.31 | 1037434.31 | 4208047 | Import from HNF-12 Maskal NJY feeder due to load changeover
38 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F01-SEETHAKALLU | 819.13 | 808.72 | 15000 | 0.015 | 0 | 0 | 223200 | 0.2232 | 202124 | 0.20212 | 9083645 | 1097396.84 | 1116564.84 | 9064477 | Import from UF-05 Kalenahalli NJY feeder due to load changeover
39 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F02-MYDALA | 1102.51 | 1078.54 | 0 | 0 | 63000 | 0.063 | 176700 | 0.1767 | 162300.6 | 0.1623 | 32965169.5 | 1899345.14 | 21150663.1 | 13713851.54 | Export to UF-04 Urdigere Rural feeder due to load changeover
40 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F03-D.DURGA | 685.57 | 675.71 | 0 | 0 | 0 | 0 | 197200 | 0.1972 | 178358 | 0.17836 | 8557786 | 961521.58 | 961512.58 | 8557795
41 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F04-URDIGERE-RURAL | 648.99 | 636.25 | 63000 | 0.063 | 0 | 0 | 317800 | 0.3178 | 287529 | 0.28753 | 11030030 | 1552496.26 | 1553588.26 | 11028938 | Import from UF-02 Mydala NJY feeder due to load changeover
42 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F05-KALENAHALLI | 572.36 | 560.51 | 0 | 0 | 15000 | 0.015 | 222000 | 0.222 | 202524 | 0.20252 | 31165691.99 | 2421663.8 | 21258806.82 | 12328548.97 | Export to UF-01 Seethkallu feeder due to load changeover
43 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F06-KURUVELU | 622.59 | 614.79 | 0 | 0 | 0 | 0 | 156000 | 0.156 | 141128 | 0.14113 | 9284926 | 761917.08 | 762070.08 | 9284773
44 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F07-SATHAGHATTA | 1348.75 | 1318.43 | 0 | 0 | 0 | 0 | 303200 | 0.3032 | 292826.8 | 0.29283 | 58887896.6 | 3375976.05 | 39292955.62 | 22970917.03
45 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F08-HALUGONDANAHALLI | 774.36 | 763.06 | 0 | 0 | 0 | 0 | 226000 | 0.226 | 204548 | 0.20455 | 8740949 | 1104245.57 | 1105912.57 | 8739282
46 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HEBBUR_66 | F15-NIDUVALALU -NJY | 700.08 | 0 | 21000 | 0.021 | 0 | 0 | 21000 | 0.021 | 19558 | 0.019558 | 4905031.1 | 257174.02 | 3670349.02 | 1491856.1 | Import from RSD-2 SUB-DIVISON CONSUMPTION
47 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNENAHALLI_66 | F02-HONNENAHALLI IP | 4858.1 | 0 | 120000 | 0.12 | 0 | 0 | 120000 | 0.12 | 111348 | 0.11135 | 2992470 | 601938.71 | 600290.71 | 2994118 | Import from RSD-2 SUB-DIVISON CONSUMPTION
50 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F05-NJY-KITTAGANAHALLY | 632.59 | 0 | 15000 | 0.015 | 0 | 0 | 15000 | 0.015 | 13644 | 0.013644 | 1193834.01 | 132396.44 | 1008160.44 | 318070.01 | Import from CSD-1 SUB-DIVISON CONSUMPTION
51 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F06-SANKAPURA | 157.93 | 0 | 23000 | 0.023 | 0 | 0 | 23000 | 0.023 | 21409 | 0.021409 | 778053.06 | 132797.58 | 130030.59 | 780820.05 | Import from CSD-1 SUB-DIVISON CONSUMPTION
52 | NON-RAPDRP | KYATSANDRA |  |  | F08-BEGUR | 697.13 | 0 | 4800 | 0.0048 | 0 | 0 | 4800 | 0.0048 | 4407 | 0.004407 | 262235.01 | 50980.51 | 155315.51 | 157900.01 | Import from CSD-1 SUB-DIVISON CONSUMPTION
53 | NON-RAPDRP | KYATSANDRA |  |  | F13-DASARAHALLI NJY | 257.65 | 0 | 5500 | 0.0055 | 0 | 0 | 5500 | 0.0055 | 5170 | 0.00517 | 5 | 35311.92 | 477.92 | 34839 | Import from RSD-2 SUB-DIVISON CONSUMPTION

## Feederwise Energy Audit (2) (hidden)
Feeder to Consumer Audit (August-24 INPUT and September-24 DCB)
SL. No. | AREA- RAPDRP/Non_RAPDRP/sharing between RAPDRP & Non_RAPDRP | Sub Division | O&M Section | STATION | FEEDER NO.& NAME (as per MDM) |  |  | BILLED CONSUMPTION (Metered Sales) in Units | Unmetered consumption (LT4a/ SL/ WS) in Units | Remarks (Assessed Energy/ Import/ Export/Others) | REMARKS & Reasons for -ve, above 10% for T & D LOSS | REMARKS & Reasons for-ve above 10% for AT&C LOSS | Action Plan for reducing the T&D LOSS | Methodology adopted to achieve T&Dloss below 3% | REMARKS & Reasons for-ve above 10% for AT&C LOSS
[6 empty] | TOTAL IMPORT IN UNITS | TOTAL EXPORT IN UNITS
1 | 1a | 2 | 3 | 4 | 5 | 21=(20*A)+B | 25=(24*C)+D | 32 | 33 | 47 | 48 |  |  |  | 49
1 | RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F08-BADDIHALLI | 0 | 0 | 791994.5 | 378 | Street Light Installation Consumption on this feeder Estimation to be Prepared | 0 | 0 | 817372.5 | 0.81737
2 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F09-KESARAMODU-NJY | 0 | 0 | 743703 | 0 |  | 0 | 0 | 743703 | 0.7437
3 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F10-CM-EXTENSION | 0 | 638000 | 85520 | 0 | Export to RAPDRP area | 0 | 0.638 | 85520 | 0.08552
4 | RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F10-CM-EXTENSION | 638000 | 0 | 579692.4 | 0 | Import from RAPDRP area | 0.638 | 0 | 579692.4 | 0.57969
5 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F11-KALAHALLI | 0 | 32000 | 8273 | 24400 | Export to F01 KITTAGANAHALLI & F12 KESARAMADU IP feeder due to load changeover | 0 | 0.032 | 32673 | 0.032673
6 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F12-KESARAMODU | 21000 | 0 | 147 | 67978 | Import from F-11 Kallahalli feeder due to load changeover | 0.021 | 0 | 68125 | 0.068125
7 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F14-SKS | 0 | 581900 | 59414.5 | 945 | Newly charged feeder, Installations yet to be tagged Energy is exported to F09-Maranayakanapalya feeder | 0 | 0.5819 | 60359.5 | 0.06036
8 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F01-CIPSA | 0 | 0 | 408740 | 0 | Dedicated Feeder | 0 | 0 | 408740 | 0.40874
9 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F03-HARALURU | 73300 | 0 | 1677 | 114098 | Import from HF-11 Raitharapalya feeder due to load changeover | 0.0733 | 0 | 115775 | 0.11578
10 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F04-INCAP | 0 | 0 | 774186 | 0 |  | 0 | 0 | 774186 | 0.77419
11 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F05-INDUSTRIAL | 120000 | 0 | 971616 | 0 | Import from HF-07 Carmobile feeder due to load changeover | 0.12 | 0 | 1446616 | 1.4466
12 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F06-K-M-HALLI | 100210 | 0 | 2150 | 154674 | Import from HF-12 Nandihalli feeder due to load changeover | 0.10021 | 0 | 156824 | 0.15682
13 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F07-CARMOBILES | 0 | 120000 | 483298.75 | 0 | Export to HF-05 Industrial feeder due to load changeover & Sharing with Dabuspet Subdivision | 0 | 0.12 | 1377298.75 | 1.3773
14 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F08-HIREHALLI | 0 | 0 | 379 | 27917 |  | 0 | 0 | 28296 | 0.028296
15 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F09-MARNAYAKANAPALYA | 90000 | 0 | 366445 | 15362 | Import from HF-10 S S MUTT feeder due to load changeover | 0.09 | 0 | 381807 | 0.38181
16 | RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F09-MARNAYAKANAPALYA | 581900 | 0 | 507983 |  | Import from F14-SKS feeder RAPDRP area | 0.5819 | 0 | 507983 | 0.50798
17 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F10-SIDDAGANGA-MATA | 0 | 90000 | 72589 | 378 | Export to HF-09 M N feeder due to load changeover | 0 | 0.09 | 72967 | 0.072967
18 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F11-RAITHARAPALYA | 0 | 73300 | 426288 | 0 | Export to HF-03 Haralur feeder due to load changeover | 0 | 0.0733 | 426288 | 0.42629
19 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F12-NANDIHALLI-NJY | 0 | 300800 | 329226.4 | 0 | Export to HF-06 K M HALLI feeder due to load changeover & Sharing with Dabuspet Subdivision | 0 | 0.3008 | 910705.4 | 0.91071
20 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F14-RANE WALES | 0 | 0 | 88000 | 0 | Dedicated Feeder | 0 | 0 | 513000 | 0.513
21 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | HIREHALLY_66 | F15-KOLIHALLI | 0 | 0 | 0 | 43969 |  | 0 | 0 | 43969 | 0.043969
22 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNENAHALLI_66 | F03-KARENAHALLI IP | 0 | 0 | 1009 | 87562 |  | 0 | 0 | 88571 | 0.088571
23 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNENAHALLI_66 | F04-HONASIGERE IP | 0 | 0 | 0 | 22633 |  | 0 | 0 | 22633 | 0.022633
24 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F01-THAVAREKERE | 76700 | 0 | 357 | 132238 | Import from HNF-12 Maskal NJY feeder due to load changeover | 0.0767 | 0 | 132595 | 0.13259
25 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F02-MULUKUNTE | 0 | 0 | 219 | 23006 |  | 0 | 0 | 23225 | 0.023225
26 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F03-HONNUDIKE | 45600 | 0 | 114 | 81658 | Import from HNF-08 Honnudike NJY feeder due to load changeover | 0.0456 | 0 | 81772 | 0.081772
27 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F04-SASALU | 0 | 0 | 128 | 51843 |  | 0 | 0 | 51971 | 0.051971
28 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F05-HOLAKALLU | 56401 | 0 | 9 | 109801 | Import from HNF-10 HOLAKALLU NJY feeder due to load changeover | 0.056401 | 0 | 109810 | 0.10981
29 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F06-CHOLAMBALLI | 12950 | 0 | 330 | 50333 | Import from HNF-09 CNNL feeder due to load changeover | 0.01295 | 0 | 50663 | 0.050663
30 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F07-VIRUPASANDRA | 0 | 7000 | 36 | 23916 | Exported units belongs to RSD-2 Sub-Division | 0 | 0.007 | 23952 | 0.023952
31 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F08-HONNUDIKE-NJY | 0 | 45600 | 314279.3 | 0 | Export to HNF-03 Honnudike feeder due to load changeover | 0 | 0.0456 | 314279.3 | 0.31428
32 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F09-CNNL | 0 | 12950 | 976 | 0 | Single Water Supply Installation Sales not Recorded Consumption export to HNF-06 Cholamballi IP feeder | 0 | 0.01295 | 976 | 0.000976
33 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F10-HOLAKALLU-NJY | 0 | 56401 | 152897 | 0 | Export to HNF-05 HOLAKALLU feeder due to load changeover | 0 | 0.056401 | 152897 | 0.1529
34 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F11-ARENAHALLI | 0 | 0 | 111260.5 | 0 |  | 0 | 0 | 111260.5 | 0.11126
35 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F12-MAASKAL | 0 | 76700 | 131867.4 | 0 | Export to HNF-01 Thavarekere feeder due to load changeover | 0 | 0.0767 | 131867.4 | 0.13187
36 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F13-VAHINI PIPES | 0 | 0 | 1056233 | 0 | Dedicated Feeder | 0 | 0 | 1056233 | 1.0562
37 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNUDIKE_66 | F14-JOLUMARANAHALLI | 0 | 0 | 1 | 56139 |  | 0 | 0 | 56140 | 0.05614
38 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F01-SEETHAKALLU | 0 | 0 | 390 | 64670 |  | 0 | 0 | 65060 | 0.06506
39 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F02-MYDALA | 0 | 0 | 202686 | 0 |  | 0 | 0 | 202686 | 0.20269
40 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F03-D.DURGA | 0 | 0 | 43 | 62067 |  | 0 | 0 | 62110 | 0.06211
41 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F04-URDIGERE-RURAL | 0 | 0 | 477 | 81111 |  | 0 | 0 | 81588 | 0.081588
42 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F05-KALENAHALLI | 0 | 0 | 231459 | 0 |  | 0 | 0 | 231459 | 0.23146
43 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F06-KURUVELU | 0 | 0 | 235 | 45627 |  | 0 | 0 | 45862 | 0.045862
44 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F07-SATHAGHATTA | 0 | 0 | 279210.5 | 0 |  | 0 | 0 | 279210.5 | 0.27921
45 | NON-RAPDRP | KYATSANDRA | URDIGERE | URDIGERE_66 | F08-HALUGONDANAHALLI | 0 | 0 | 615 | 79422 |  | 0 | 0 | 80037 | 0.080037
46 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HEBBUR_66 | F15-NIDUVALALU -NJY | 18000 | 0 | 16409 | 0 | Import from RSD-2 SUB-DIVISON CONSUMPTION | 0.018 | 0 | 16409 | 0.016409
47 | NON-RAPDRP | KYATSANDRA | HONNUDIKE | HONNENAHALLI_66 | F02-HONNENAHALLI IP | 36000 | 0 | 154 | 32597 | Import from RSD-2 SUB-DIVISON CONSUMPTION | 0.036 | 0 | 32751 | 0.032751
50 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F05-NJY-KITTAGANAHALLY | 11000 | 0 | 10067 | 378 | Import from CSD-1 SUB-DIVISON CONSUMPTION | 0.011 | 0 | 10445 | 0.010445
51 | NON-RAPDRP | KYATSANDRA | KYATSANDRA | BADDIHALLI_66 | F06-SANKAPURA | 10200 | 0 | 3294 | 6030 | Import from CSD-1 SUB-DIVISON CONSUMPTION | 0.0102 | 0 | 9324 | 0.009324
52 | NON-RAPDRP | KYATSANDRA |  |  | F08-BEGUR | 5200 | 0 | 4800.23 | 0 | Import from CSD-1 SUB-DIVISON CONSUMPTION | 0.0052 | 0 | 4800.23 | 0.0048002
53 | NON-RAPDRP | KYATSANDRA |  |  | F13-DASARAHALLI NJY | 1600 | 0 | 1454 | 0 | Import from RSD-2 SUB-DIVISON CONSUMPTION | 0.0016 | 0 | 1454 | 0.001454
Sub division TOTAL | [5 empty] | 1803111 | 1836000 | 9222332.48 | 1461130
Station Auxillary (Input & Sales)
EHT Consumption
Above 11KV Wheeled Energy/ Open Access
IPP Consumption
Sub Division Grand Total | [5 empty] | 1803111 | 1836000 | 9222332.48 | 1461130